## Sheet1
Reverse osmosis specific energy consumption calculation
c | 0.1 | wt% | Concentration of salt in supply water
π | 0.75 | bar | Osmotic pressure of supply water
ρ | 1001 | kg/m3 | Density of supply water
CF | 4 | - | Concentration factor: ratio of retentate to feed concentration, CF = 1/(1-R) when there is ~100% rejection (R being the recovery)
SEC | 0.73671 | kWh/m3 | Specific energy consumption
PRO | 7 | bar | RO “pure water” operational pressure: pressure required to generate permeate in the absence of an osmotic pressure
Ploss,RO | 1.6 | bar | System pressure losses, mainly associated with the RO membrane element channels
ԑpump | 60 | % | Mechanical-electrical efficiency of the pump: the percentage of supplied electrical power which does useful work
ԑturb | 85 | % | Efficiency of the energy recovery turbine: the percentage of latent mechanical energy in the retentate which is usefully recovered
Eci | 0.1 | kWh/m3 | SEC of ancillary operations (e.g. instrumentation and control)