## Slide 1
Energy and Flexibility Modelling
LECTURE 13 POWER SYSTEM FLEXIBILITY
1

## Slide 2
Course Name
MINI LECTURE NUMBER & NAME
Mini Lecture Learning Objective
2
Learning Outcomes
By the end of this lecture, you will be able to:
ILO1: Understand the challenge of integrating renewables into the power system
ILO2: Understand the value of flexibility in the power system and how to plan for it
ILO3: Identify the sources of flexibility on the supply side and their required characteristics
ILO4: Identify the sources of flexibility on the demand side and their required characteristics
Notes: By the end of this lecture, you will be able to:
1) Understand the challenge of integrating renewables into the power system.
2) Understand the value of flexibility in the power system and how to plan for it.
3) Identify the sources of flexibility on the supply side and their required characteristics.
4) Identify the sources of flexibility on the demand side and their required characteristics.

## Slide 3
3
13.1.1 Accelerating growth of renewables
13.1 VRE integration challenge
Variable renewable energy (VRE), mainly solar and wind, have become cheaper than conventional thermal and nuclear power plants and their share in power generation is growing rapidly.
Solar and wind are indigenous resources, and their rapid growth reduces fuel security concerns. However, the growing penetration of VRE in the power system is causing concerns for the reliable provision of electricity.
Source: IRENA 2019a
Notes: Energy transition for keeping global temperature rise below 2 degrees requires major structural changes to power systems around the world. Electrification of end-use sectors such as industry, buildings, and transport, as well as rigorous decarbonization of the power sector are key for the energy transition. Decarbonizing the power sector requires a transformation from a system mainly based on fossil fuels to one based on renewable energy.
Variable renewable sources, mainly solar and wind, have become cheaper than conventional thermal and nuclear power plants, and their share in power generation is growing rapidly. Large-scale integration of these variable renewables into the power system, although challenging, is essential for decarbonizing the power sector while continuing to meet the growing demand for energy. Furthermore, solar and wind are indigenous resources and their rapid growth reduces fuel security concerns in many regions. However, the growing penetration of variable renewables in the power system, which is primarily built on inflexible demand and dispatchable thermal generation, is causing concerns for the reliable provision of electricity. Therefore there is a growing call for a fast increase of flexibility in power systems in order to reliably accommodate a larger share of variable renewables.
The share of electricity in the total final energy demand is expected to increase from 20% in 2015 to 40% in 2050. According to IRENA REmap, renewable sources will supply more than 86% of the global electricity generated and the variable renewable sources will supply more than 60% of the electricity generated.

## Slide 4
4
13.1.2 System integration challenge
13.1 VRE integration challenge
The system balancing and renewable integration challenge is commonly assessed over three timescales:
Stability and resilience: The system's ability to recover from disturbance (in seconds).
Balancing and operational security: The ability of the system to retain the balance of demand (Minutes to days).
Adequacy: The ability of the electricity system to supply the peak and aggregate electrical demand within an area at all times (Months to years).
Recovering from disturbance & balancing unpredictable fast changes
Operating reserve & Inertia
Now
Seconds
Minutes
Hours
Days
Months
Years
Load following: balancing forecast errors (in load and generation) and variability in the net load
Real time balancing
Intra-day balancing
Day-ahead balancing
Annual and seasonal balancing /Capacity planning
Investment
Hydro/Maintenance scheduling
Source: IRENA 2018a
Notes: Power systems must be actively managed to maintain a steady balance between supply and demand. This is a complex task as demand varies continuously and demand forecasts commonly include errors. The level of uncertainty rises for extended timescales and will be greatest when consumers respond to an unexpected, shared stimulus, such as a cold snap in the weather. The other major source of uncertainty is the loss of one or more generators or transmission lines. Therefore variability and uncertainty are common phenomena in power system operation. In the present fossil fuel dominated systems, the resulting imbalances from demand variation and uncertainty are managed mainly by dispatchable thermal power plants.
The output of variable renewable resources ramps up and down quickly depending on the available resources, and forecasting their output is difficult. Therefore integrating higher shares of variable renewable energy in the power system introduces additional, rather than new, variability and uncertainty to the system on the supply side.
The system balancing and renewable integration challenge is commonly assessed over three timescales:
• Stability and resilience: The system's instantaneous ability to recover from instantaneous disturbance and imbalances in supply and demand and maintain the operating reserve and inertia.
• Balancing and operational security: The system's ability to retain the balance of demand and supply known as load following. It includes real-time, intra-day, and day-ahead balancing.
• Adequacy: The electricity system's ability to supply the peak and aggregate electricity demand at all times under normal operating conditions.

## Slide 5
5
13.1.3 The net load
13.1 VRE integration challenge
The net load is the power demand after accounting for variable renewable output.
As the share of renewables grows the difference between the power demand and the net load increases.
The balancing challenge will be greatest at times that demand for electricity and the output from variable power plants are changing simultaneously in opposite directions.
Source: IRENA 2020a
Notes: Traditionally, power systems are designed to deal with demand-related variations and uncertainty. Electricity demand profile depends on various factors such as local weather, GDP, and social and cultural factors. However, power demand usually follows a regular pattern in each region. It is generally easier to forecast fluctuations in demand than in variable renewable supply.
An important characteristic of the power system is net load. The net load is the power demand after accounting for variable renewable output. At low penetration of renewables, the difference between net load and power demand is insignificant. However, as the share of renewables grows, the difference between the two increases. The balancing challenge, therefore, lies in the ability of the system to react quickly enough to accommodate such extensive and rapid changes and retain the system stability.
The balancing challenge will be greatest at times that demand for electricity and the output from variable power plants are changing simultaneously in opposite directions. The two extreme cases of this happen as follows:
• At times that high electricity demand is falling to a minimum while the output for variable renewables is increasing to the peak
•When electricity demand is rising towards peak while V.R.E. output is falling.

## Slide 6
6
13.1.4 Key integration challenges
13.1 VRE integration challenge
Source: IRENA 2018a
Over-generation & avoiding VRE curtailment
Increased ramping rate
Increased ramping range
Uncertainty & forecast errors
System stability & meeting the inertia requirements
Notes: There are five key challenges that arise from the large-scale integration of variable renewable electricity sources:
Firstly the frequency of occurrence and magnitude of forecast errors on net load increases as the share of V.R.E grows. These lead to higher cycling of thermal generation and over-generation. In some cases, power generated in the system is more than demand, due to technical constraints on the rate and the extent that thermal generators can reduce their output. To maintain frequency at its nominal value, the system operator has to curtail power generation from variable renewables. Curtailment is a risk mitigation measure that is usually applied when a system cannot cope with the balancing issues due to lack of flexibility. V.R.E. curtailment reduces renewable generators' capacity factor and their economic attractiveness; it also reduces the system-wide benefits of V.RE. Therefore bridging flexibility gaps is key for having a reliable integration of renewables into the power system.
Secondly, The resultant ramping rate in the net load can be higher than demand and renewable generation output. As the share of variable renewables increases, the ramping rate in the net load increases as well.
In addition to increasing ramping rates, V.R.E. increases ramping ranges which is the difference between the minimum and maximum loads. Therefore conventional dispatchable units need to cycle faster and more frequently to meet the new ramping requirements. Flexible generation capacity needs to be sufficient to cover increased ramping range requirements. If the system cannot cope with net load down ramping requirement, it has to curtail the V.R.E. output. Similarly, if the system cannot cope with the net load upward ramping requirement, it might lead to loss of load.

## Slide 7
7
13.1.5 Key integration challenges
13.1 VRE integration challenge
Over-generation & avoiding VRE curtailment
Increased ramping rate
Increased ramping range
Uncertainty & forecast errors
System stability & meeting the inertia requirements
Source: IRENA 2018a
Notes: To deal with uncertainty, power systems regulation requires some amount of reserve capacity to be procured at each time. The first purpose of the reserve capacity is to help the system recover in case of a contingency (for example, loss of generation). This can be achieved through a fast-acting frequency containment reserve to restore the frequency to its nominal value. The second purpose of the reserve capacity is to compensate for demand forecast errors (also called regulating reserve). As the share of variable renewable generation grows, V.R.E. forecast errors (rather than demand forecast errors) become the main source of net load uncertainty and, therefore, the main driver of regulating reserve requirements.
Lastly, a very high share of V.R.E. is that it poses system reliability risks related to lack of system inertia. Power system inertia refers to the total instantaneous inertia from the spinning rotors of synchronous generators. Such inertia helps generators resist changes in their rotational speed from system imbalances and gives system operators time to activate necessary controls to recover the system. Inertia is related to the amount of online conventional synchronous capacity at each time, and it is inversely proportional to the rate of change of frequency. In other words, the lower the inertia, the faster the change in frequency, the more difficult it is to maintain reliable operations. The power system has specific requirements for inertia that impose having some synchronous capacity online.

## Slide 8
Course Name
MINI LECTURE NUMBER & NAME
Mini Lecture Learning Objective
8
Lecture 13.1 References
IRENA (2019a), “Global energy transformation: A roadmap to 2050” (2019 edition), International Renewable Energy Agency, Abu Dhabi, www.irena.org/publications/2019/Apr/Global-energy-transformation-A-roadmap-to-2050-2019Edition
IEA (2011), “Harnessing Variable Renewables: a guide to balancing Challenge” (2011), International Energy Agency (IEA). https://www.oecd.org/publications/harnessing-variable-renewables-9789264111394-en.htm
IEA(2020), “Power system in transition, Challenges and opportunities ahead for electricity security”, 2020, International Energy Agency (IEA) https://www.iea.org/reports/power-systems-in-transition
IRENA (2018a), “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2019b), “Solution to integrate high shares of variable renewable energy” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Jun/Solutions-to-integrate-high-shares-of-variable-renewable-energy

## Slide 9
9
13.2.1 Flexibility of the power system
13.2 Power System Flexibility
Flexibility of the power system refers to:
Flexibility is measured in terms of megawatts (MW) available for ramping up and down, over time.
"The ability of a power system to reliably and cost-effectively manage the variability and uncertainty of demand and supply across all relevant timescales"
Notes: The rate, extent, that is the difference between the minimum and maximum, and the frequency of variations in the net load specifies the flexibility requirements of the system. Higher variable renewable penetration increases one or more of these factors. Therefore, estimating the net load profile over various variable renewable shares is crucial in planning for flexibility as it indicates the portion of the load to be supplied by dispatchable (controllable) generators.
According to the International Energy Agency, the flexibility of the power system refers to "The ability of a power system to reliably and cost-effectively manage the variability and uncertainty of demand and supply across all relevant timescales".
In other words, it expresses the ability of a power system to maintain a reliable balance of supply and demand in the face of rapid, large expected and unexpected imbalances.
Flexibility is measured in terms of megawatts (or MW) available for ramping up and down over time. In order to reliably integrate large capacities of renewable electricity generation into the power system, planners must ensure that sufficient flexibility resources and balancing capability are available.

## Slide 10
10
13.2.2 Flexible power systems
13.2 Power System Flexibility
Avoid loss of loads and meets the peak demand and peak net loads.
Maintain a reliable balance of supply and demand at all times.
Incorporate adequate storage potential through sector coupling and investment in storage capacities to balance periods of high VRE generation and low demand, as well as periods of high demand but low VRE generation.
Incorporate demand-side management measures in order to adjust demand to respond to periods of supply shortages and over-generation.
Ensure an adequate supply of ancillary services in order to maintain system capabilities to mitigate risks in case of possible destabilizing events.
Improve operation practices and incorporate market restructuring to unlock flexibility potential.
Notes: According to IRENA a power system is considered to be flexible if it can cost-effectively, reliably and across all time scales do the following:
1) Avoids loss of loads and meet the peak demand and peak net loads. Therefore lost load is one of the measures often used for flexibility risk assessment of a system or scenarios for system transition.
2) Maintains a reliable balance of supply and demand at all times by ensuring:
  •the availability of sufficient capability to ramp up and down demand or supply or both, through ensuring minimum reserve capacity and minimum inertia limit.
  •the availability of adequate fast-starting capacity
  •a system that can operate safely during low net loads
Reserve inadequacy is another measure used to assess the flexibility risks in a system.
3) Incorporates adequate storage potential through sector coupling and investment in storage capacities to balance high V.R.E. generation periods and periods of high demand but low V.R.E. generation and avoid curtailment. Power spillage (that is, the amount of variable renewable electricity that is not used) and amount of power curtailment are other measures often used for flexibility assessment.
4) Incorporates demand-side management measures to adjust demand to respond to periods of supply shortages and over-generation.
5) Ensures an adequate supply of ancillary services to maintain system capabilities to mitigate possible destabilizing events.
6) Improves operation practices and incorporate market restructuring to unlock the flexibility potential of the network.

## Slide 11
11
13.2.3 Flexibility resources in the power system
13.2 Power System Flexibility
Power systems can use a range of flexibility resources in demand, supply, and operation to manage the variations in the net load.
The potential and availability of these solutions vary from region to region.
In order to achieve the goals of the energy transition, flexibility should be harnessed in all sectors of the energy system.
Power system flexibility
Sector coupling
Demand-Side
Management
Storage
Electric Vehicles
Gas
Heat
Transmission
Distribution
Generation
H2
Source: IRENA 2019b
Notes: The flexibility in the power system is traditionally associated with dispatchable thermal plants. However, power systems can use a range of flexibility resources to manage the variations in the net load. The types and potentials of these resources vary from region to region.
According to IRENA these solutions include “the geographic distribution of variable renewable electricity generators, pooling of resources, restructuring markets to remunerate flexibility, enhancing grid infrastructure, deploying advanced battery technologies, developing demand-side management programmes and enhancing the cycling capabilities of thermal generators. Sector coupling also provides flexibility to the system with the power to heat, power to gas and exploiting the storage potential via E.V. charging.”
To reliably accommodate higher shares of renewables in the power system, we should unlock the full flexibility potential of the energy system, and flexibility should be harnessed in all sectors of the energy system. Identifying the potential and availability of flexibility resources in a power system is critical to further advance and achieve the energy transition goals.

## Slide 12
12
13.2.4 Planning for flexibility
13.2 Power System Flexibility
Source: IRENA 2019c
Notes: The flexibility of a power system depends on how the power system has developed over time, based on resources, policies, and growth path. The size, level of modernization of a power system, and demand growth prospects are key flexibility attributes. For example, demand growth stalls in many large, modern systems due to industrialization reaching maturity and an emphasis on energy efficiency. Therefore the system faces overcapacity that was built to support past demand growth, with many of the thermal power plants depreciating. Thus the system has to invest in costly retrofitting options, and investment in new assets will be more costly.
In developing regions, however, planning for flexibility is easier. New capacity should be built to supply the growing demand and this provides the opportunity to embed flexibility measures in market design and grid codes for new assets.
Planning for flexibility is a continuous, complex multi-step process and requires accounting for all possible sources. Many different factors should be taken into account, and that form a complex mathematical problem that should be solved using appropriate tools. As the share of V.R.E. grows, power systems goes through a transition. A detailed study of the system is needed to consider both technical and institutional aspects of flexibility, while final decisions are usually made based on least-cost principles. It is sensible to plan ahead for flexibility rather than exploring suboptimal investments after flexibility issues arise in a power system. Here we review the flexibility assessment method outlined by IRENA.

## Slide 13
13
13.2.5 Flexibility assessment
13.2 Power System Flexibility
Step 3: Assess future flexibility
1. Optimize VRE using geospatial optimization
Optimize VRE capacity mix
Estimate VRE production based on location and policy goals
Estimate future net-load
2. Least-cost capacity expansion to identify future assets
Study the net-load to assess needs for cycling
Optimize non-VRE capacity mix based on future technologies
Identify additional flexibility assets (e.g. , storage, DSM)
Assess benefits of sector coupling
3. Repeat step 1
Assess operability of long-term plans identified in previous steps
Step 1: Assess current flexibility
1. Production cost modelling
Assess current levels of curtailment and loss of load
Assess over-generation incidents and fluctuation of price
Assess cycling of units (start-up ramping and min gen incidents)
Assess if operating reserves are adequate
2. Network studies
Assess if system can efficiently regulate frequency and voltages
Assess if system can recover from unexpected events
Assess if system has sufficient inertia
Assess if transmission elements get overloaded
Step 2: Bridge gaps following least-cost approach
1. Unlock existing flexibility
Regulatory, market changes
Dispatch units based on merit order
Train staff at generating units to operate plants flexibly
Pooling with neighbors
Adjust operating reserves based on new needs
2. Implement demand side management (DSM) schemes
3. Invest in new assets
  Transmission enhancement
  Retrofit existing units
  Invest in new generation and/or storage
If flexibility gaps are identified go to step 2. Else directly to step 3
Source: IRENA 2018a
Notes: The flexibility assessment process starts with an assessment of current flexibility gaps and extends into the future. Depending on the system's present state, integration measures might be necessary for the future or may already be a matter of urgency. This greatly changes the list of available options and associated costs. The method has three steps:
The first step is assessing the current flexibility status and identifying inexpensive and investment-free ways to unlock existing flexibility through improvements in operational practices and market restructuring. The main aim of the flexibility assessment of an existing system is to:
identify current flexibility gaps,
assess the maximum share of V.R.E. that can be integrated without significantly changing the non-V.R.E. component of the grid,
estimate the time left until the existing flexibility is exhausted
identify a least-cost set of solutions to unlock existing flexibility
In the next steps, if flexibility gaps are identified, mitigation measures can be simulated and assessed for their effectiveness and compared based on their costs and benefits; otherwise, after identifying a pathway to exploit existing flexibility, a long-term assessment should be conducted to complement the planning process. The main goal of a long-term flexibility assessment is identifying future investments in generation, transmission, and storage and exploring the full long-term flexibility potential of demand-side management programmes and sector coupling.
The methodology suggests using one or more tools with specific computational capabilities such as geospatial planning, dispatch simulation, and long-term capacity expansion. Such tools can optimize system operations and investments at time scales that are representative of electricity markets.

## Slide 14
Course Name
MINI LECTURE NUMBER & NAME
Mini Lecture Learning Objective
14
Lecture 13.2 References
IRENA (2018a), “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2019b), “Solution to integrate high shares of variable renewable energy” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Jun/Solutions-to-integrate-high-shares-of-variable-renewable-energy
IEA (2011), “Harnessing Variable Renewables: a guide to balancing Challenge” (2011), International Energy Agency (IEA). https://www.oecd.org/publications/harnessing-variable-renewables-9789264111394-en.htm
IRENA (2019c), “Innovation landscape for a renewable-powered future: Solutions to integrate variable renewables” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Feb/Innovation-landscape-for-a-renewable-powered-future

## Slide 15
15
13.3.1 Flexible generation
13.3 Supply-side flexibility
Peak generators
Mid-merit generators
Baseload generators
Source: IRENA 2018a
Notes: Currently, dispatchable generators are the largest source of flexibility on the supply side. According to I.E.A., "A flexible generator is one with fast ramping capabilities, a low minimum operating level and fast start-up and shutdown times". Three major groups of generation technologies can be identified based on their ability to alter their output:
Baseload units usually have limited cycling capabilities and cannot ramp up or down their output quickly. Baseload technologies usually require a large upfront investment. However, they can produce large amounts of power at a relatively low operating cost. Therefore, they are used to supply the non-variable part of power demand. An example of a baseload unit is a nuclear plant.
Peak generators usually have opposite techno-economic characteristics; they require a lower upfront investment but higher operating cost. Peak generators have a very flexible operation and have the characteristics of rapid start-up and shut down, fast ramping capabilities, and low minimum operational level. Therefore they are suitable for fast response to short-term variability over peak hours and forecast errors. Peak generators usually have very low capacity factors and have a different business model compared to baseload units. Examples of peak generation units are open cycle gas turbines and internal combustion generators.
Mid-merit generators can be used either as baseload or peak load and usually have a slower response rate compared to peak generators. They can provide flexibility within an hour and are used for load following and supplying the intermediate demand. Examples of intermediate generators are combined-cycle gas turbines and hydropower.

## Slide 16
16
13.3.2 Flexible generation
13.3 Supply-side flexibility
Key questions about the flexibility provided by dispatchable generation to the system:
What is installed capacity of each dispatchable technology? (MW)
How fast can each ramp up/down its output? (MW/minute)
How quickly can it start up/shut down?
What is the minimum stable output level?
Source: IRENA 2018a
Notes: There have been growing attempts to improve the flexibility provided by thermal generations as the V.R.E. sources are gradually becoming the mainstay of the power system. Modern designs of thermal generators offer improved performance, such as higher ramping rates and faster start-up, especially for coal and gas technologies.
Nuclear power plants have varying levels of flexibility, and some have the technical ability to ramp up or down relatively rapidly. According to I.E.A., some nuclear plants' operation data show that in the load-following mode, they can ramp up from 30% to 100% in one hour (and vice-versa). However, this capability may be constrained to contingency use for economic or security reasons.
In a system with a high share of V.R.E., limited curtailment of V.R.E. can also be a very cost-effective source of flexibility and provide down-regulation. Geographic dispersion of V.R.E. resources can also reduce the congestion on transmission and provide more flexibility to the system. In deregulated markets, flexibility is gradually becoming an important revenue source as generators should respond to price signals; therefore, flexibility gets remunerated. In regulated environments, increasing the flexibility of existing plants through retrofitting plans is gaining attention as a short to medium-term solution.
In summary, there are four key questions that should be answered to assess the flexibility provided by dispatchable generators:
• What is the installed capacity of each dispatchable technology?
• How fast can each unit ramp up or down its output?
• How quickly can it start up or shut down?
• What is the minimum stable output level?

## Slide 17
17
13.3.3 Energy storage
13.3 Supply-side flexibility
Months
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Pumped Hydro, CAES
Power to gas
Batteries
Flywheels
Key questions about the flexibility provided by energy storage to the system:
What is installed capacity of each storage type? (MW)
How fast it can be charged/discharged? (MW/minute)
What is the maximum energy storage capacity? (MWh)
Does the storage unit have the ability to provide inertia to the system?
Source: IRENA 2020a, IRENA2018a
Notes: The primary purpose of electricity storage is to shift electricity supply over time by storing electricity when its value is the lowest and discharging when its value is the highest. The attributed value of electricity storage in this context comes from reductions in the overall generation cost by avoiding V.R.E. curtailment, reducing thermal plants operation cycles, and preventing more expensive generators from running. Storage can facilitate high shares of V.R.E. by mitigating their impact on grid operations. We previously discussed that the impacts of V.R.E. vary over different time scales. Hence, to maximize their value for the power system, storage technologies should have appropriate technical characteristics across different time scales such as fast response time and ability to provide inertia.
At the shortest time scale (seconds), storage technologies such as pumped hydro and synchronous flywheels can provide inertia and reduce a system’s dependence on thermal generators for providing inertia. At a time scale of seconds to minutes, storage is mainly used for balancing and provision of operational reserves. Technologies such as pumped hydro, the power to gas, and state of the art long-duration batteries are used for balancing over more extended periods and between seasons.
In summary, there are four key questions that should be answered in order to assess the flexibility provided by an energy storage unit:
• What is the installed capacity of each storage type?
• How fast it can be charged and discharged?
• What is the maximum energy storage capacity?
• Can the storage unit provide inertia?

## Slide 18
18
13.3.4 Grid Flexibility
13.3 Supply-side flexibility
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Interconnectors & Transmission
Months
Key questions about flexibility provided through interconnection/transmission in a regions:
What is interconnection/transmission capacity to neighbouring regions/countries? (MW)
Is there a limit on the rate at which it can be operated? (MW / minute)
Does the connection provide inertia to the system?
Source: IRENA 2018a
Notes: Grid flexibility through expanding interconnection and transmission lines allows the shared use of flexible resources to manage variability among connected regions. Therefore, while the storage balances supply and demand over time, transmission and interconnection balance that over space. Grid flexibility bridges supply-side and demand-side flexibility.
Therefore, low flexibility in the grid could become a bottleneck to the system flexibility. For example, in a system with high supply-side flexibility, the congestion in the grid could still limit integrating high shares of V.R.E. Furthermore, inertia between two systems can be shared through synchronous connections (via A.C.). For example, since the interconnection between Ireland and the UK is direct current (or D.C.), the two regions cannot share inertia.
The maximum flexibility capacity (power ramp) provided by an interconnection or transmission line is approximately equal to twice its rated capacity. This rated capacity is equal to the overall power ramping provided if the transmission line exporting at maximum capacity can switch to importing at maximum capacity.
Therefore, there are three key questions that should be answered in order to assess the flexibility provided by a transmission or interconnector line:
• What is interconnection and transmission capacity to neighbouring regions and countries?
• Is there a limit on the rate at which it can be operated?
• Does the connection provide inertia to the system?

## Slide 19
19
13.3.5 Operation flexibility
13.3 Supply-side flexibility
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Pooling of resources
Intra-day market & Improved VRE forecasting
Co-optimised hydro-thermal unit commitment
Months
Examples of key questions about the flexibility provided by operation practices into the system:
Does the regulatory framework and market structure encourage the power exchange between regions?
Does the current market structure incentivize investment in the flexible generation?
Can the time step for planning the day ahead and intra-day market balancing be reduced?
Can improved VRE forecasts be incorporated into market planning?
Source: IRENA 2018a
Notes: The last source of flexibility on the supply-side is operational flexibility, which is about the regulatory framework and the market environment surrounding the power system. Operational flexibility includes investment free solutions for unlocking the system's flexibility by improving how the assets in the power system are operated. The market and regulatory frameworks act as an inhibitor to existing technical flexibility on the supply-side and demand-side. Centralized dispatching and building a market based on price merit to schedule electricity exchanges are examples of operation mechanisms that could facilitate investment and coordination to unlock the flexibility in the power system.
Operation flexibility can also exist in different time scales to address different flexibility issues. In the medium to short-term, the use of modern forecast technologies and reducing the time step of day-ahead and intra-day market balancing are operational measures that can reduce the impact of V.R.E. uncertainty on the system. In the long-term, regulators can provide better long-term price signals to incentivize investment in flexible resources by increasing the time and space granularity of wholesale markets or restructuring the capacity market.
Therefore various questions should be answered to assess the potential for unlocking flexibility in the power system through operational measures such as:
•Does the regulatory framework and market structure incentivize the power exchange between regions?
•Does the market structure incentivize investment in the flexible generation?
•Can the time step for the day ahead planning and intra-day market balancing be reduced?
•Can improved V.R.E. forecasts be incorporated into market planning?

## Slide 20
Course Name
MINI LECTURE NUMBER & NAME
Mini Lecture Learning Objective
20
Lecture 13.3 References
IRENA (2018a), “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2019d), “Innovation landscape brief: Utility-scale batteries” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Sep/Enabling-Technologies
IRENA (2020a), “Electricity storage valuation framework: Assessing system value and ensuring project viability” (2020), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2020/Mar/Electricity-Storage-Valuation-Framework-2020
IRENA (2020b), “Innovation landscape brief: Advanced forecasting of variable renewable power generation” (2020), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2020/Jul/System-Operation-Innovation-Landscape-briefs
IRENA (2020c), “Innovation landscape brief: Co-operation between transmission and distribution system operators” (2020), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2020/Jul/System-Operation-Innovation-Landscape-briefs

## Slide 21
21
13.4.1 Flexibility resources on the demand side
13.4 Demand-side flexibility
Therefore, as with other resources, some key questions need to be answered to assess the technical capacity of flexibility resources on the demand side:
What is the size of the demand-side resource in terms of the total demand that can be curtailed or shifted? (MW)
How fast can the demand be curtailed/shifted? (MW / minute)
Is there a limit on the duration of curtailment/shift? (MWh)
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Aggregators providing demand-side flexibility
EVs
Power to heat
Power to gas
Industrial/Commercial demand response providing reserve
Months
Source: IRENA 2018a, IRENA 2019e
Notes: Traditionally demand was considered inflexible in the power system, and the power system operators adjusted the supply to match the electricity demand. However, as the share of variable renewable sources is increasing, the supply-side is becoming less flexible. Therefore demand needs to become more flexible. Demand-side flexibility refers to shifting or curtailing consumer demand and implies transitioning to a system in which demand can be modified to better match electricity supply.
I.E.A. categorize demand-side flexibility resources as managed resources and responsive resources. Managed resources are consumers, usually industrial or commercial, that adjust their electricity consumption based on long-term direct control agreements. These resources are contracted in advance by a system operator to reduce their consumption for a certain number of hours per year. This implies that a certain proportion of the consumer's demand can be postponed without economic hardship.
A responsive resource is the proportion of consumer's demand that the system can rely on to respond dynamically, through price signals, to scarcity or surplus of electricity by decreasing or increasing consumption.
Therefore three key questions need to be answered to assess the technical capacity of flexible resources on the demand side:
• What is the size of the demand-side resource in terms of the total demand that can be curtailed or shifted?
• How fast can the demand be curtailed or shifted?
• Is there a limit on the duration of curtailment or shift?

## Slide 22
22
13.4.2 Demand aggregators
13.4 Demand-side flexibility
Source: IRENA 2019f
Notes: Consumers participating in demand response and management have various sizes ranging from individual residential and commercial consumers to large industrial consumers. They are located in different zones on the power network. One of the key challenges of demand response is to form a coordination of loads of various size to meet the required response rates or capacity reduction in different nodes.
One way of increasing responsiveness is to aggregate demand from end-users of various sizes and form a larger demand block. Aggregators are companies that contract with different end-users and distributed energy resource owners to control their assets on their behalf. Aggregators then act as a participant in the electricity and ancillary services market by controlling assets belonging to end-users and aggregate them to operate as a single demand-side response block. To do so, aggregators could use smart metering or smart appliances that can respond automatically to price signals from the system.
Another measure to facilitate demand-response is adopting the time-of-use rates that change based on power market prices to provide incentives for reducing consumption during peak hours. Time-of-use pricing can also support V.R.E. by increasing demand during over-generation and adjusting demand to reduce netload ramps. As a result, the need for conventional peak capacity in the power system and the cycling of the thermal generations reduces. As in the case of other resources, there is a limit on the maximum demand response capacity. The economic and technical effectiveness of demand response is at a maximum during the early stages and decreases as this capacity increases.

## Slide 23
23
13.4.3 Sector coupling: Power to heat & Power to gas
13.4 Demand-side flexibility
Source: https://pixabay.com/photos/smart-home-house-technology-3920905/
Notes: Electrification is an essential part of the energy transition. If electrification and sector coupling takes place in a way that is controllable, the electrified demand can be a source of flexibility.
Coupling the heat and power sectors through electrification of heat can increase peak power demand and ramping requirements and impose additional reliability risks on a system if not well planned. However, if the electrification of heat is done smartly, it can contribute to V.R.E. integration and decarbonization of the power grid. A heating system composed of a heat pump and thermal storage can provide flexibility to the power system by generating heating at times when there is abundant renewable energy in the system and electricity prices are low. This energy can be stored in thermal storage and used at a later stage to supply heat demand when variable renewable generation is low, or electricity prices are high.
Hydrogen is another low carbon energy vector that could have a key role in the deep decarbonization of the energy sector. Hydrogen can be produced from renewable power via electrolysers. Electrolysers are devices that use electricity to split water into hydrogen and oxygen. Electrolysers can provide demand-side flexibility and balancing services by adjusting hydrogen production to follow the variable renewable generators in periods of high resource availability. The produced hydrogen can be injected into the gas grid and reduce the carbon intensity of the gas network. It can also be stored in underground gas storage facilities, providing cheap seasonal storage for the excess renewable.

## Slide 24
24
13.4.4 Sector coupling: Power to EV
13.4 Demand-side flexibility
Source: https://pixabay.com/photos/ev-charging-vehicle-electric-5704430/
Notes: Same as heating, electrification is one of the key options for decarbonizing transport. In this case, the sector coupling is facilitated via Electric Vehicles (or E.V.). Electric vehicles can have different charging strategies. Their charging pattern would significantly affect the implications of electrifying transport for the power system. The charging strategies can be divided into two main groups:
Uncontrolled charging is an inflexible charging strategy and implies that electric vehicles will charge at maximum power when they are plugged in. Therefore there will be a swift surge in the power demand if many electric vehicles are connected to the grid, simultaneously posing reliability risks for the power grid. Uncontrolled charging increases the peak power demand and the power grid's ramping rate requirements, which could cause flexibility issues for the power grid.
The other group is referred to as smart charging. IRENA defines this as: "a way of optimising the charging process according to distribution and/or transmission grid constraints, local availability of renewable energy sources and customers' preferences". If electric vehicles are charged smartly, they can provide demand-side flexibility to the power grid by adjusting their charging to follow the availability of the variable renewable sources and avoiding the peak hours. Therefore, the availability of the infrastructure for smart charging of electric vehicles reduces the stress on the power grid from the additional load for electrifying transportation. It could also facilitate the integration of a higher amount of solar and wind to the power system through load shifting and providing reserves.

## Slide 25
25
13.4.5 Flexibility assessment tools
13.4 Power System Flexibility
Tier 1 tools mainly provide a qualitative comparison of different power systems and, therefore, do not require a lot of data.
Tier 2 tools do a flexibility sufficiency check without performing full power system optimization. These tools are mainly aimed at screening the potential flexibility issues, using time series and dispatch data from an external tool.
Tier 3 tools are based on unit commitment and dispatch models and are sometimes combined with capacity planning models. Tier 3 models are complex and require a lot of data.
The IRENA FlexTool is a Tier 3 model and analyses system operations and flexibility of a system over one year horizon.
Notes: There are various tools for Flexibility assessment using different methods and with different levels of complexity. IRENA categorises different approaches for flexibility assessment into three categories of assessment tools, based on their complexity and their level of details:
• Tier 1 tools mainly provide a qualitative comparison of different power systems and, therefore, do not require a lot of data.
• Tier 2 tools do a flexibility sufficiency check without performing complete power system optimization. Tier 2 tools are mainly aimed at screening the potential flexibility issues using time series and dispatch data from an external tool.
• Tier 3 tools are based on unit commitment and dispatch models and are sometimes combined with capacity planning models.
These models provide a detailed picture of the power system operation and evolution in different scenarios and provide a solid foundation for flexibility assessment. However, Tier 3 models are complex and require a lot of data. In this course, we use IRENA FlexTool for the assessment of flexibility in a power system. The FlexTool is a Tier 3 model and analyses system operations and flexibility of a system over one year horizon. The FlexTool is data-driven and uses a general unit commitment model structure; therefore, the input data have a major role in specifying what the model does.

## Slide 26
Course Name
MINI LECTURE NUMBER & NAME
Mini Lecture Learning Objective
26
Lecture 13.4 References
IRENA (2018a), “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2019e), “Demand-side flexibility for power sector transformation” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Dec/Demand-side-flexibility-for-power-sector-transformation
IRENA (2019f), “Innovation landscape brief: Aggregators” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org//media/Files/IRENA/Agency/Publication/2020/Jul/IRENA_Aggregators_2020.pdf?la=en&hash=34E90050F80DD1B012F2E6C9E4C90EE11BED6A82
IRENA (2019g), “Innovation landscape brief: Time-of-use tariff” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Jun/Market-Design-Innovation-Landscape-briefs
IRENA (2019h), “Hydrogen: A renewable energy perspective” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Hydrogen_2019.pdf