## Slide 1
Assessing power system flexibility with IRENA FlexTool
LECTURE 1
POWER SYSTEM FLEXIBILITY FOR THE ENERGY TRANSITION

## Slide 2
2
Learning Outcomes
By the end of this lecture, you will be able to:
ILO1: Understand the challenge of integrating renewables into the power system
ILO2: Learn the implications of flexibility issues through the use of country cases
ILO3: Understand the value of flexibility in the power system and how to plan for it
ILO4: Get an overview of this course in Flexibility assessment using FlexTool

## Slide 3
3
1.1.1 Energy transition in the power sector
1.1 Transformation of Power Systems
Source: IRENA (2019)
Future power systems must rely on renewable sources to align with international climate agreements.
In the coming decades, solar and wind will emerge as the primary sources of electricity generation.
Notes: Keeping global temperature rise below 2°C, as outlined in the Paris Agreement, requires a fundamental transformation of the global energy system—from one predominantly reliant on fossil fuels to a more energy-efficient and renewable-based system.
IRENA’s global energy transition roadmap, REmap, suggests that renewables could supply two-thirds of total primary energy globally by 2050. Large-scale electrification of end-use sectors—such as buildings, industry, and transport—along with the progressive decarbonization of the power sector, will be critical to this transition.
To achieve this, the share of renewable energy in the power sector must more than triple compared to current levels, with variable renewable energy (VRE) sources like solar and wind accounting for 60% of total electricity generation as shown in the slide. This implies that many countries will need to gradually transform their power systems, making solar and wind the backbone of electricity supply.

## Slide 4
Chart: Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Solar | 10 | 10 | 10 | 10 | 10 | 50 | 200 | 350 | 550 | 720 | 910 | 1200 | 1150 | 1100 | 1070 | 1010 | 900 | 640 | 350 | 80 | 10 | 10 | 10 | 10
Wind | 4300 | 4010 | 3700 | 3450 | 3120 | 2800 | 2540 | 2230 | 2000 | 1850 | 1600 | 1520 | 1400 | 1460 | 1570 | 2010 | 2480 | 2980 | 3430 | 3850 | 4100 | 4210 | 4280 | 4300
4
1.1.2 Variable Renewable Energy (VRE)
1.1 Transformation of Power Systems
Source: Gairola & Bindra (2019)
VRE sources, primarily solar and wind, fluctuate based on irradiation levels and wind speed.
While they exhibit some typical patterns, their generation remains highly uncertain due to variations in meteorological conditions.
Notes: Variable Renewable Energy (VRE) refers to renewable energy sources whose electricity generation varies due to natural fluctuations in resources like sunlight and wind. The two primary types of VRE are solar power, which depends on solar radiation and is affected by cloud cover, time of day, and seasonal changes, and wind power, which fluctuates with wind speed and varies by location. Unlike conventional power plants, which can be dispatched based on demand, VRE sources produce electricity intermittently, requiring careful integration into power systems. Key characteristics of VRE include intermittency, meaning their output is not constant and cannot be fully controlled; forecasting challenges, as production depends on weather conditions; and geographical dependence, since wind and solar resources are stronger in some locations than others.
The slide presents a typical graph illustrating the output of solar and wind power plants over time. The x-axis represents time (hours), while the y-axis represents power output (MW). Solar power generation follows a bell-shaped curve, beginning at sunrise, peaking around midday when sunlight is strongest, and dropping to zero at sunset. In contrast, wind power generation tends to be higher at night, gradually decreasing after sunrise, reaching its lowest point around midday, and rising again in the late afternoon and evening. This pattern occurs because wind speeds typically increase at night due to temperature differences between the land and atmosphere, then decrease in the morning as solar heating stabilizes atmospheric conditions.

## Slide 5
5
1.1.3 Residual load (net load)
1.1 Transformation of Power Systems
Source: EIA (2014)
The net load is the power demand after accounting for variable renewable output.
As the share of VRE grows, the difference between the power demand and the net load increases.
Notes: Traditionally, power systems are designed to deal with demand-related variations and uncertainty. Electricity demand profile depends on various factors such as local weather, GDP, and social and cultural factors. However, power demand usually follows a regular pattern in each region. It is generally easier to forecast fluctuations in demand than in variable renewable supply.
An important characteristic of the power system is residual load or net load. The net load is the power demand after accounting for variable renewable output. At low penetration of renewables, the difference between net load and power demand is insignificant. However, as the share of VRE grows, the difference between the two increases. The balancing challenge, therefore, lies in the ability of the system to react quickly enough to accommodate such extensive and rapid changes and retain the system stability.
The balancing challenge will be greatest at times that demand for electricity and the output from variable power plants are changing simultaneously in opposite directions. The two extreme cases of this happen as follows:
• At times that high electricity demand is falling to a minimum while the output for variable renewables is increasing to the peak
•When electricity demand is rising towards peak while V.R.E. output is falling.
The slide shows a set of three graphs comparing the electricity load, net load, and renewable energy generation (solar and wind) for three different days in California (USA) in 2014: April 22, July 22, and October 22. The top row shows the total electricity load (brown line) and the net load (blue line), which is the remaining demand after accounting for renewable energy generation. The bottom row illustrates the contributions of solar (yellow area) and wind (blue area) power throughout the day. The July 22 graph shows the highest peak demand and the greatest solar generation, while the net load is lowest around midday due to high solar output. In contrast, April and October exhibit lower total loads, with wind generation being more stable but solar having a smaller impact. These graphs highlight the variability of net load due to the fluctuating contributions of wind and solar energy.

## Slide 6
6
1.1 Transformation of Power Systems
Source: IRENA (2018)
Over-generation & avoiding VRE curtailment
Increased ramping rate and ramping range
Uncertainty & forecast errors
System stability & meeting the inertia requirements
1.1.4 Key integration challenges
Notes: There are four key challenges that arise from the large-scale integration of variable renewable electricity sources:
Firstly the frequency of occurrence and magnitude of forecast errors on net load increases as the share of V.R.E grows. These lead to higher cycling of thermal generation and over-generation. In some cases, power generated in the system is more than demand, due to technical constraints on the rate and the extent that thermal generators can reduce their output. To maintain frequency at its nominal value, the system operator has to curtail power generation from variable renewables. Curtailment is a risk mitigation measure that is usually applied when a system cannot cope with the balancing issues due to lack of flexibility. V.R.E. curtailment reduces renewable generators' capacity factor and their economic attractiveness; it also reduces the system-wide benefits of VRE.
Secondly, The resultant ramping rate in the net load can be higher than demand and renewable generation output. As the share of variable renewables increases, the ramping rate in the net load increases as well. In addition to increasing ramping rates, V.R.E. increases ramping ranges which is the difference between the minimum and maximum loads. Therefore conventional dispatchable units need to cycle faster and more frequently to meet the new ramping requirements. Flexible generation capacity needs to be sufficient to cover increased ramping range requirements. If the system cannot cope with net load down ramping requirement, it has to curtail the V.R.E. output. Similarly, if the system cannot cope with the net load upward ramping requirement, it might lead to loss of load.
Thirdly, to deal with uncertainty, power systems regulation requires some amount of reserve capacity to be procured at each time. The first purpose of the reserve capacity is to help the system recover in case of a contingency (for example, loss of generation). This can be achieved through a fast-acting frequency containment reserve to restore the frequency to its nominal value. The second purpose of the reserve capacity is to compensate for demand forecast errors (also called regulating reserve). As the share of variable renewable generation grows, V.R.E. forecast errors (rather than demand forecast errors) become the main source of net load uncertainty and, therefore, the main driver of regulating reserve requirements.
Lastly, a very high share of V.R.E. is that it poses system reliability risks related to lack of system inertia. Power system inertia refers to the total instantaneous inertia from the spinning rotors of synchronous generators. Such inertia helps generators resist changes in their rotational speed from system imbalances and gives system operators time to activate necessary controls to recover the system. Inertia is related to the amount of online conventional synchronous capacity at each time, and it is inversely proportional to the rate of change of frequency. In other words, the lower the inertia, the faster the change in frequency, the more difficult it is to maintain reliable operations. The power system has specific requirements for inertia that impose having some synchronous capacity online.

## Slide 7
7
1.1.5 System integration challenges
1.1 Transformation of Power Systems
Recovering from disturbance & balancing unpredictable fast changes
Operating reserve & Inertia
Now
Seconds
Minutes
Hours
Days
Months
Years
Load following: balancing forecast errors (in load and generation) and variability in the net load
Real time balancing
Intra-day balancing
Day-ahead balancing
Annual and seasonal balancing /Capacity planning
Investment
Hydro/Maintenance scheduling
Source: IRENA (2018)
The system balancing and renewable integration challenge is commonly assessed over three timescales:
Stability and resilience: The system's ability to recover from disturbance (in seconds).
Balancing and operational security: The ability of the system to retain the balance of demand (Minutes to days).
Adequacy: The ability of the electricity system to supply the peak and aggregate electrical demand within an area at all times (Months to years).
Notes: Power systems must be actively managed to maintain a steady balance between supply and demand. This is a complex task as demand varies continuously and demand forecasts commonly include errors. The level of uncertainty rises for extended timescales and will be greatest when consumers respond to an unexpected, shared stimulus, such as a cold snap in the weather. The other major source of uncertainty is the loss of one or more generators or transmission lines. Therefore variability and uncertainty are common phenomena in power system operation. In the present fossil fuel dominated systems, the resulting imbalances from demand variation and uncertainty are managed mainly by dispatchable thermal power plants.
The output of variable renewable resources ramps up and down quickly depending on the available resources, and forecasting their output is difficult. Therefore integrating higher shares of variable renewable energy in the power system introduces additional, rather than new, variability and uncertainty to the system on the supply side.
The system balancing and renewable integration challenge is commonly assessed over three timescales:
• Stability and resilience: The system's instantaneous ability to recover from instantaneous disturbance and imbalances in supply and demand and maintain the operating reserve and inertia.
• Balancing and operational security: The system's ability to retain the balance of demand and supply known as load following. It includes real-time, intra-day, and day-ahead balancing.
• Adequacy: The electricity system's ability to supply the peak and aggregate electricity demand at all times under normal operating conditions.

## Slide 8
8
Lecture 1.1 References
Abhinav Gairola, Hitesh Bindra, Chapter Three - Nuclear-Wind Powered Microgrid: Reduced-Order Modeling of LWR Response, Editor(s): Hitesh Bindra, Shripad Revankar, Storage and Hybridization of Nuclear Energy, Academic Press, 2019, Pages 31-48, ISBN 9780128139752, https://doi.org/10.1016/B978-0-12-813975-2.00003-X.
EIA. 2014. Increased solar and wind electricity generation in California are changing net load shapes. Online article. https://www.eia.gov/todayinenergy/detail.php?id=19111
IRENA. 2018. “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition

## Slide 9
9
1.2.1 Curtailment: China’s Wind Power in the North
1.2 VRE Integration Challenges in Context
Wind-rich regions in China faced severe curtailment due to limited transmission and rigid dispatch policies.
China’s case shows that infrastructure upgrades must be paired with regulatory flexibility to enable effective renewable integration.
Source: Luo et al. (2018)
Notes: China’s experience with wind energy integration highlights a significant flexibility challenge in modern power systems: aligning rapid renewable deployment with grid infrastructure and policy frameworks. In the early 2010s, China invested aggressively in wind power, especially in its northern and northwestern provinces like Inner Mongolia, Gansu, and Xinjiang. These regions offered abundant wind resources but were located far from major demand centers on the eastern coast. Due to limited transmission capacity and inadequate regional coordination, large volumes of wind energy had to be curtailed. In 2016, curtailment rates exceeded 30% in some areas as shown in the figure, wasting clean energy and undermining investor confidence.
This curtailment problem was not solely technical; it was also institutional. Historically, local grid operators had economic and regulatory incentives to dispatch coal-fired power, which led to renewable generators being shut out even when wind power was available. Moreover, regional dispatch systems and inflexible grid operations made it difficult to accommodate variable renewable energy. Recognizing these constraints, Chinese authorities launched a multifaceted response that included massive investments in ultra-high voltage (UHV) transmission lines, policy reforms mandating renewable integration quotas, and the beginning of electricity market liberalization to promote more dynamic dispatch systems.
Thanks to these interventions, China’s wind curtailment rate dropped to below 3% by 2023. The country’s efforts demonstrate how technical investments (like UHV transmission) must be paired with regulatory and market reforms to achieve real flexibility. China’s case offers a powerful lesson: physical infrastructure alone is not sufficient, systems must evolve institutionally to prioritize clean energy dispatch, enable regional coordination, and incentivize flexibility services such as storage and demand response.

## Slide 10
10
1.2.2 Ramping Capacity: California’s Duck Curve
1.2 VRE Integration Challenges in Context
Source: Elements (2022)
In systems with a high penetration of solar energy, net load decreases and increases sharply throughout the day.
These abrupt changes in net load can potentially lead to instability in the grid.
Notes: California provides one of the most iconic examples of the challenges associated with integrating high shares of variable renewable energy, particularly solar PV. As the state has aggressively expanded rooftop and utility-scale solar installations, midday solar production has increasingly exceeded demand, pushing net load (total demand minus renewable generation) to very low levels during the afternoon. This trend creates what is known as the "duck curve", a graph where the shape of net load resembles the silhouette of a duck as illustrated in the figure. The steep ramp-up in electricity demand during the late afternoon, when solar generation rapidly declines, places significant stress on the system’s flexibility.
This pattern has intensified over the past decade. For instance, California Independent System Operator (CAISO) has observed net load ramps exceeding 13 GW in just a few hours during spring evenings, a pace that challenges even fast-ramping natural gas plants. Without sufficient flexible resources (such as energy storage or demand response), this can lead to reliability concerns or even curtailment of solar generation. Moreover, during mild weather conditions, the net load can approach zero or even go negative, forcing the grid operator to export excess power or shut down clean generation. These issues highlight the temporal mismatch between solar availability and peak consumption.
In response, California has implemented several measures to address this flexibility challenge. These include large-scale deployment of battery energy storage systems, time-of-use pricing to shift demand, and greater integration with neighboring regional markets to absorb excess solar. Notably, battery systems like the Moss Landing Energy Storage Facility are now playing a critical role in flattening the duck curve by absorbing excess solar energy and discharging it during the evening peak. California’s experience underscores the importance of pairing renewable energy expansion with system flexibility, a combination of infrastructure, market design, and smart grid management to ensure reliability in a high-VRE future.

## Slide 11
11
1.2.3 Grid Congestion: Germany’s North-South Transmission Bottleneck
1.2 VRE Integration Challenges in Context
Most wind power is generated in northern Germany, far from demand centers in the south.
Transmission constraints lead to frequent curtailment of renewable energy.
Grid congestion reflects a spatial flexibility challenge in integrating high shares of renewables.
Source: Clean Energy Wire (2016)
Notes: Germany has undergone a major energy transition (Energiewende) that has led to a rapid increase in wind and solar generation. A large share of this renewable capacity, particularly wind, is located in the northern regions of the country, while the industrial and population centers that demand the most electricity are in the south. This geographic imbalance has created significant strain on the existing transmission infrastructure, as power must be moved over long distances from where it is generated to where it is consumed.
Because the expansion of high-voltage transmission lines has lagged behind renewable development, the result has been frequent grid congestion. When transmission capacity is insufficient to accommodate the available renewable generation, grid operators are forced to curtail renewable output or redispatch conventional generation, often at high cost. In 2023 alone, Germany curtailed nearly 19 TWh of renewable electricity, primarily from wind farms. This not only results in wasted clean energy but also imposes significant operational and economic burdens on the power system.
These curtailments highlight a core flexibility challenge in Germany’s energy system: the ability to balance supply and demand across space in real time. Even though Germany has made major strides in integrating renewable energy, the physical limits of the grid have become a key bottleneck. The mismatch between the pace of renewable deployment and the development of grid infrastructure serves as a critical lesson for countries pursuing high shares of variable renewables: flexibility is not just about time, but also about location.

## Slide 12
12
1.2.4 Inertia and Stability: A High-Wind System in Ireland
1.2 VRE Integration Challenges in Context
High shares of wind power have reduced system inertia, increasing frequency instability risks.
Ireland’s grid relies on a cap to manage non-synchronous generation in real time.
Low inertia require new system services to maintain grid stability.
Source: Amperon (2024)
Notes: Ireland has emerged as a global leader in the integration of wind energy, with wind providing approximately 40% of annual electricity generation. On particularly windy days, non-synchronous generation (mainly wind and HVDC interconnectors) can meet over 70% of instantaneous demand. However, this rapid shift away from conventional synchronous generators (like gas or coal plants) has brought new operational challenges. One of the most critical is the reduction in system inertia, which traditionally comes from the rotating mass of synchronous machines and helps stabilize grid frequency during disturbances.
With lower inertia, Ireland’s power system is more vulnerable to rapid changes in frequency following generator outages or sudden changes in load. These events can lead to high rates of change of frequency (RoCoF), potentially triggering further disconnections or even cascading failures if not managed carefully. To mitigate this risk, the transmission system operator, EirGrid, initially imposed a limit on the share of non-synchronous generation at any given time, known as the System Non-Synchronous Penetration (SNSP) limit. This operational cap effectively curtailed wind generation to maintain system stability, even when conditions were favorable.
To address these stability issues without compromising renewable integration, Ireland launched the DS3 Programme (Delivering a Secure, Sustainable Electricity System). This initiative introduced new system services, including fast frequency response, inertia-like capabilities from grid-forming inverters, and the deployment of synchronous condensers to simulate the stabilizing effect of traditional generators. As a result, the SNSP limit has gradually been raised from 50% to 75%, with a long-term goal of 95%. Ireland’s experience illustrates that grid stability and VRE integration must be managed together, especially in small or isolated systems with limited interconnection capacity.

## Slide 13
13
Lecture 1.2 References
Luo, G., Dan, E., Zhang, X., & Guo, Y. (2018). Why the wind curtailment of northwest China remains high. Sustainability (Switzerland), 10(2). https://doi.org/10.3390/su10020570
Elements (2024). The Solar Power Duck Curve Explained. Online article: https://elements.visualcapitalist.com/the-solar-power-duck-curve-explained/
Clean Energy Wire (2016). Re-dispatch costs in the German power grid. Online article: https://www.cleanenergywire.org/factsheets/re-dispatch-costs-german-power-grid#
Amperon (2024). How strong winds in Ireland left power market stakeholders exposed. Online article: https://www.amperon.co/blog/how-strong-winds-in-ireland-left-power-market-stakeholders-exposed

## Slide 14
14
1.3.1 Power system flexibility
1.3 Flexibility in power systems
Flexibility of the power system refers to:
Flexibility is measured in terms of megawatts (MW) available for ramping up and down, over time.
"The ability of a power system to reliably and cost-effectively manage the variability and uncertainty of demand and supply across all relevant timescales"
Notes: The rate, extent, that is the difference between the minimum and maximum, and the frequency of variations in the net load specifies the flexibility requirements of the system. Higher variable renewable penetration increases one or more of these factors. Therefore, estimating the net load profile over various variable renewable shares is crucial in planning for flexibility as it indicates the portion of the load to be supplied by dispatchable (controllable) generators.
According to the International Energy Agency, the flexibility of the power system refers to "The ability of a power system to reliably and cost-effectively manage the variability and uncertainty of demand and supply across all relevant timescales".
In other words, it expresses the ability of a power system to maintain a reliable balance of supply and demand in the face of rapid, large expected and unexpected imbalances.
Flexibility is measured in terms of megawatts (or MW) available for ramping up and down over time. In order to reliably integrate large capacities of renewable electricity generation into the power system, planners must ensure that sufficient flexibility resources and balancing capability are available.

## Slide 15
15
1.3.2 Flexible power systems
1.3 Flexibility in power systems
No loss of load
Balance of supply and demand
Adequate storage capacity
Demand-side management
Supply of ancillary services
Good operational and market practices
Notes: According to IRENA a power system is considered to be flexible if it can cost-effectively, reliably and across all time scales do the following:
1) Avoids loss of loads and meet the peak demand and peak net loads. Therefore lost load is one of the measures often used for flexibility risk assessment of a system or scenarios for system transition.
2) Maintains a reliable balance of supply and demand at all times by ensuring:
  •the availability of sufficient capability to ramp up and down demand or supply or both, through ensuring minimum reserve capacity and minimum inertia limit.
  •the availability of adequate fast-starting capacity
  •a system that can operate safely during low net loads
Reserve inadequacy is another measure used to assess the flexibility risks in a system.
3) Incorporates adequate storage potential through sector coupling and investment in storage capacities to balance high V.R.E. generation periods and periods of high demand but low V.R.E. generation and avoid curtailment. Power spillage (that is, the amount of variable renewable electricity that is not used) and amount of power curtailment are other measures often used for flexibility assessment.
4) Incorporates demand-side management measures to adjust demand to respond to periods of supply shortages and over-generation.
5) Ensures an adequate supply of ancillary services to maintain system capabilities to mitigate possible destabilizing events.
6) Improves operation practices and incorporate market restructuring to unlock the flexibility potential of the network.

## Slide 16
16
1.3.3 Flexibility resources in the power system
1.3 Flexibility in power systems
Power systems can use a range of flexibility resources in demand, supply, and operation to manage the variations in the net load.
The potential and availability of these solutions vary from region to region.
In order to achieve the goals of the energy transition, flexibility should be harnessed in all sectors of the energy system.
Power system flexibility
Sector coupling
Demand-Side
Management
Storage
Electric Vehicles
Gas
Heat
Transmission
Distribution
Generation
H2
Source: IRENA. (2018)
Notes: The flexibility in the power system is traditionally associated with dispatchable thermal plants. However, power systems can use a range of flexibility resources to manage the variations in the net load. The types and potentials of these resources vary from region to region.
According to IRENA these solutions include “the geographic distribution of variable renewable electricity generators, pooling of resources, restructuring markets to remunerate flexibility, enhancing grid infrastructure, deploying advanced battery technologies, developing demand-side management programmes and enhancing the cycling capabilities of thermal generators. Sector coupling also provides flexibility to the system with the power to heat, power to gas and exploiting the storage potential via E.V. charging.”
To reliably accommodate higher shares of renewables in the power system, we should unlock the full flexibility potential of the energy system, and flexibility should be harnessed in all sectors of the energy system. Identifying the potential and availability of flexibility resources in a power system is critical to further advance and achieve the energy transition goals. We will explore these resources in more detail in Lecture 2 of this course.

## Slide 17
17
1.3.4 Planning for flexibility
1.3 Flexibility in power systems
Source: IRENA. (2019)
Notes: The flexibility of a power system depends on how the power system has developed over time, based on resources, policies, and growth path. The size, level of modernization of a power system, and demand growth prospects are key flexibility attributes. For example, demand growth stalls in many large, modern systems due to industrialization reaching maturity and an emphasis on energy efficiency. Therefore the system faces overcapacity that was built to support past demand growth, with many of the thermal power plants depreciating. Thus the system has to invest in costly retrofitting options, and investment in new assets will be more costly.
In developing regions, however, planning for flexibility is easier. New capacity should be built to supply the growing demand and this provides the opportunity to embed flexibility measures in market design and grid codes for new assets.
Planning for flexibility is a continuous, complex multi-step process and requires accounting for all possible sources. Many different factors should be taken into account, and that form a complex mathematical problem that should be solved using appropriate tools. As the share of V.R.E. grows, power systems goes through a transition. A detailed study of the system is needed to consider both technical and institutional aspects of flexibility, while final decisions are usually made based on least-cost principles. It is sensible to plan ahead for flexibility rather than exploring suboptimal investments after flexibility issues arise in a power system. Here we review the flexibility assessment method outlined by IRENA.

## Slide 18
18
1.3.5 Flexibility assessment
1.3 Flexibility in power systems
Step 3: Assess future flexibility
1. Optimize VRE using geospatial optimization
Optimize VRE capacity mix
Estimate VRE production based on location and policy goals
Estimate future net-load
2. Least-cost capacity expansion to identify future assets
Study the net-load to assess needs for cycling
Optimize non-VRE capacity mix based on future technologies
Identify additional flexibility assets (e.g. , storage, DSM)
Assess benefits of sector coupling
3. Repeat step 1
Assess operability of long-term plans identified in previous steps
Step 1: Assess current flexibility
1. Production cost modelling
Assess current levels of curtailment and loss of load
Assess over-generation incidents and fluctuation of price
Assess cycling of units (start-up ramping and min gen incidents)
Assess if operating reserves are adequate
2. Network studies
Assess if system can efficiently regulate frequency and voltages
Assess if system can recover from unexpected events
Assess if system has sufficient inertia
Assess if transmission elements get overloaded
Step 2: Bridge gaps following least-cost approach
1. Unlock existing flexibility
Regulatory, market changes
Dispatch units based on merit order
Train staff at generating units to operate plants flexibly
Pooling with neighbors
Adjust operating reserves based on new needs
2. Implement demand side management (DSM) schemes
3. Invest in new assets
  Transmission enhancement
  Retrofit existing units
  Invest in new generation and/or storage
If flexibility gaps are identified go to step 2. Else directly to step 3
Source: IRENA. (2018)
Notes: The flexibility assessment process starts with an assessment of current flexibility gaps and extends into the future. Depending on the system's present state, integration measures might be necessary for the future or may already be a matter of urgency. This greatly changes the list of available options and associated costs. The method has three steps:
The first step is assessing the current flexibility status and identifying inexpensive and investment-free ways to unlock existing flexibility through improvements in operational practices and market restructuring. The main aim of the flexibility assessment of an existing system is to:
identify current flexibility gaps,
assess the maximum share of V.R.E. that can be integrated without significantly changing the non-V.R.E. component of the grid,
estimate the time left until the existing flexibility is exhausted
identify a least-cost set of solutions to unlock existing flexibility
In the next steps, if flexibility gaps are identified, mitigation measures can be simulated and assessed for their effectiveness and compared based on their costs and benefits; otherwise, after identifying a pathway to exploit existing flexibility, a long-term assessment should be conducted to complement the planning process. The main goal of a long-term flexibility assessment is identifying future investments in generation, transmission, and storage and exploring the full long-term flexibility potential of demand-side management programmes and sector coupling.
The methodology suggests using one or more tools with specific computational capabilities such as geospatial planning, dispatch simulation, and long-term capacity expansion. Such tools can optimize system operations and investments at time scales that are representative of electricity markets.

## Slide 19
19
Lecture 1.3 References
IRENA. 2018. “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2019), “Innovation landscape for a renewable-powered future: Solutions to integrate variable renewables” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Feb/Innovation-landscape-for-a-renewable-powered-future

## Slide 20
20
1.4.1 Course Focus
1.4 Outline of the course
FlexTool
Open source power system model
Flexibility planning
This course will introduce flexibility assessment and its use to support energy planning and policymaking. The course will focus on FlexTool.
Notes: So far in this lecture, we have discussed the importance of flexibility in power systems to ensure a reliable and effective integration of high shares of variable renewable energy (VRE). This course focuses on energy system modeling concepts and their application in assessing flexibility in future power systems.
In Lecture 2, we will introduce the main sources of flexibility on both the supply and demand sides. Lectures 3 to 8 will focus on applying FlexTool to analyze different power system scenarios while covering key theoretical concepts in power system flexibility.
Additionally, the course includes hands-on exercises where you will develop your own models and analyses, applying these skills to case studies to support future energy planning and policymaking.

## Slide 21
21
1.4.2 FlexTool Learning Outcomes
1.4 Outline of the course
Aims of the course:
Understand the challenge of integrating renewables into the power system.
Understand the value of flexibility in the power system.
Understand the methodology for the FlexTool model.
How to design a FlexTool flexibility assessment.
How to increase the flexibility of a system using different alternatives. For example, with the use of power to electric vehicles or hydrogen.
Notes: During this course you will learn a number of things. You will start by understanding the challenge of integrating renewables into the power system and the value of adding flexibility into this system.
Next, you will learn the methodological underpinnings of the FlexTool model, which can help you improve the flexibility of a power system.
You will also learn how to design a FlexTool flexibility assessment. With this, you will be able to increase the flexibility within a power system.

## Slide 22
22
1.4.3 Overview of FlexTool
1.4 Outline of the course
How to integrate renewables into the power system?
What is the value of flexibility in the power system?
What sources of flexibility are there on both the demand and supply side?
What assumptions and building blocks make up FlexTool?
How does FlexTool calculate solutions?
How do we investigate the flexibility in a case-study?
How to modify input data to make different flexibility case studies
How to increase the flexibility of a system
Power to EV, hydrogen, and heat network.
Notes: For the FlexTool course you will go through a streamlined set of lectures which builds up your knowledge and experience.
First, you will learn about the power of flexibility, then you will learn to understand the assumptions FlexTool makes, as well as how it calculates cost-optimal solutions. Then you will learn how to investigate the flexibility of a particular system, how to modify input data to make different case studies, and finally, how to increase the flexibility of a system – be it through different alternatives such as power to electric vehicles, hydrogen, or the heat network.

## Slide 23
23
1.4.4 Key outcomes of FlexTool
1.4 Outline of the course
Output group | Main output types
Flexibility indicators | Loss of load, reserve shortages, spillage, VRE curtailment
Unit dispatch | Hourly dispatch of every unit
Transmission between nodes | Hourly use of transmission lines
Costs | OPEX: fuel costs, other O&M costs, CO2 costs, penalty costs from inflexibilities CAPEX: Generation capacity investments, transmission line investments, storage investments
Marginal prices | Hourly marginal price of electricity
Ramping information | One-hour and four-hour ramps
Notes: FlexTool generates a comprehensive set of results that provide valuable insights into power system flexibility and overall performance. It calculates key flexibility indicators, such as loss of loads, reserve needs, and curtailment levels, helping to assess how well the system can accommodate variable renewable energy sources. Additionally, it models unit dispatch by simulating how different generation and storage assets operate to meet demand in an optimal way. The tool also supports capacity expansion planning, identifying the most cost-effective investments in new power plants, storage, and grid reinforcements. Furthermore, FlexTool provides a detailed breakdown of system costs, including operational expenses, fuel costs, and capital investments, enabling decision-makers to evaluate the economic implications of different scenarios. Other results include transmission between nodes, marginal prices, CO2 emissions and ramping information.

## Slide 24
24
Lecture 1.4 References
IRENA. (2020). FlexTool Basic Training. Online material. https://www.irena.org/-/media/Irena/Files/IRENA-flextool/IRENA_FlexTool_BasicTraining.pdf

## Slide 25: Thank you
www.climatecompatiblegrowth.com