## Slide 1
Assessing power system flexibility with IRENA FlexTool
LECTURE 2
SOURCES OF FLEXIBILITY IN POWER SYSTEMS

## Slide 2
2
Learning Outcomes
By the end of this lecture, you will be able to:
ILO1: Identify the main flexibility issues in power systems.
ILO2: Learn some key concepts involved in the flexibility of power systems
ILO3: Describe the sources of technical flexibility on the supply side.
ILO4: Describe the sources of technical flexibility on the demand and grid sides.

## Slide 3
3
2.1.1 Synchronous and non-synchronous generators
2.1 Key concepts in flexibility
Synchronous
Non-synchronous
Notes: Synchronous generators are traditional power generation units used in thermal, hydro, and nuclear power plants. They operate at a fixed speed, synchronized with the grid frequency (50 Hz or 60 Hz), and directly contribute to system stability by providing inertia. Their rotating mass stores kinetic energy, which helps resist sudden frequency changes and maintain grid stability. Additionally, synchronous generators can generate reactive power, supporting voltage control and ensuring reliable operation of the power system. Due to their ability to naturally stabilize the grid, they have historically been the backbone of conventional power systems.
Non-synchronous generators, on the other hand, do not have a fixed rotational speed linked to the grid frequency. They include induction generators, used in some older wind turbines and small hydro plants, as well as power electronics-based generators such as modern wind turbines, solar PV, and battery storage. Unlike synchronous machines, they require external support for voltage and frequency control, as they do not inherently provide inertia. However, power electronics allow them to offer fast frequency response and synthetic inertia, improving flexibility in renewable-dominated grids.
There are also modern grid-forming inverters which are advanced power electronic devices that enable renewable energy sources (such as solar PV, wind turbines, and battery storage systems) to provide grid-supportive functions traditionally delivered by synchronous generators. Unlike conventional grid-following inverters, which depend on an existing grid frequency to operate, grid-forming inverters can establish voltage and frequency autonomously, acting as virtual synchronous generators. They can contribute synthetic inertia, voltage regulation, and fast frequency response, helping to stabilize power systems with high shares of non-synchronous generation. These capabilities make them essential for maintaining stability in low-inertia grids, especially in isolated or renewable-dominated systems like those in Ireland, Australia, and islanded microgrids.

## Slide 4
4
2.1.2 Inertia
2.1 Key concepts in flexibility
Source: Song et al. (2023)
In the grid, inertia refers to the kinetic energy stored in spinning/synchronous generators.
The shift toward renewable energy reduces overall system inertia.
Notes: Inertia is defined as the tendency of an object in motion to remain in motion. For example, inertia is what keeps a vehicle moving when a driver stops pressing on the gas pedal. Inertia in power systems comes from the energy stored in the rotating masses of large generators and some industrial motors, which helps them resist sudden changes in speed. This stored energy plays a crucial role in maintaining grid stability, especially when a power plant fails. In such cases, inertia temporarily compensates for the lost power, buying time for control systems to respond and restore balance. This natural response lasts only a few seconds but is essential for preventing rapid frequency changes that could disrupt the grid.
Traditional power systems, which rely on synchronous generators powered by coal, hydro, and nuclear plants, provide high inertia and can quickly respond to frequency deviations. However, as the energy transition progresses, more power systems are becoming dominated by inverter-based resources such as wind, solar PV, and batteries. These technologies lack the natural rotating masses of synchronous generators, leading to lower system inertia. This reduction results in weaker grids, greater frequency instability, poorer power quality, and an increased risk of load shedding or blackouts.
The shift toward renewable energy significantly reduces overall system inertia, making the grid more vulnerable to disturbances. When thermal generation dominates, the system remains stable with sufficient inertia, but as renewables take a larger share, the system’s ability to resist disruptions weakens. Inertia is crucial for maintaining the stability and reliability of power grids—higher inertia leads to better system stability, while low inertia increases the risk of instability and even grid collapse. Addressing this challenge requires new solutions, such as synthetic inertia, fast-response storage, and advanced grid-forming inverters, to ensure a stable and resilient power system.

## Slide 5
Operating reserves
Non-event
Event
Following reserve
Regulating reserve
Tertiary
Contingency reserve
Primary (Frequency Containment Reserves)
Secondary (Frequency Restoration Reserves)
Secondary
Tertiary
Ramping reserve
5
2.1.3 Operating reserves
2.1 Key concepts in flexibility
Source: Ela et al. (2011)
Generating capacity that is readily available and can be injected into the system by the operator decision within a short period of time.
Operating reserve requirements should be continuously evaluated to account for VRE uncertainty.
Notes: A flexible power system must also be equipped to manage uncertainty. To ensure system reliability, operators must procure a certain amount of reserved capacity at all times. This reserved capacity, controlled by the system operator, has traditionally served two key purposes in conventional power systems. The first is to support system recovery in the event of a contingency (such as the sudden loss of generation) through fast-acting frequency containment reserves (FCR) and to restore frequency to its nominal level after the event using slower frequency restoration reserves (FRR). The second function is to correct demand forecast errors during normal operations, commonly referred to as regulating reserves. The classification of reserves varies across countries, but in this context, operating reserves are considered the sum of contingency and regulation reserves.
As the share of variable renewable energy (VRE) increases, forecast errors from VRE—rather than demand forecast errors—become the primary source of net load uncertainty, driving the need for regulating reserves. Consequently, operating reserve requirements must be regularly reassessed to account for VRE uncertainty. At a certain level of VRE penetration, any additional capacity will necessitate increased regulation and/or contingency reserves. Key measures to enhance operational flexibility and mitigate the impact of VRE uncertainty include advancements in forecasting technologies, frequent integration of updated VRE forecasts into market operations, and reducing the time intervals in day-ahead, intra-day, and balancing markets.

## Slide 6
6
2.1.4 Capacity margin
2.1 Key concepts in flexibility
Proportion by which the total expected available generation exceeds the maximum expected level of electricity demand.
Notes: Capacity margin is a key reliability metric in power systems that represents the extra generation capacity available beyond the expected peak demand. It is expressed as a percentage of the total available capacity and serves as a buffer to handle unexpected increases in electricity consumption or power plant outages. A sufficient capacity margin ensures that the grid can meet demand even during extreme conditions, such as heatwaves or cold snaps, when electricity use spikes.
Maintaining an appropriate capacity margin is essential for grid stability and long-term planning. If the margin is too low, the system faces a higher risk of blackouts or the need for emergency demand reduction. On the other hand, an excessively high capacity margin may indicate overinvestment in generation, leading to higher costs for consumers.

## Slide 7
7
2.1.5 Ramp rate
2.1 Key concepts in flexibility
Source: IRENA. (2019)
The rate at which the power output per unit time increases or decreases is defined as ramp rate.
Depending on the type of technology, the ramp rate can vary, affecting its contribution to system flexibility differently.
Type of technology | Average ramp rate [% Pnom/min]
Nuclear | <0.1
Hard coal | 1.5-4
Lignite | 1-2
CCGT | 2-4
OCGT | 8-12
Hydropower | 1-10
ICE | >100
Battery storage | >100
Notes: The ramp rate in power systems refers to how quickly a generator can increase or decrease its power output, typically measured in megawatts per minute (MW/min) or percentage of rated power per minute (% Pnom/min). This capability is essential for balancing supply and demand, especially in modern grids with a high share of variable renewable energy sources like wind and solar. Since these sources fluctuate rapidly due to weather conditions, power systems require fast-ramping resources such as gas turbines, hydropower, and battery storage to maintain stability. For instance, open-cycle gas turbines (OCGT) can ramp up at 20–50 MW/min, while coal-fired plants are much slower, ramping at only 1–5 MW/min. Nuclear power, due to its technical constraints, has an even lower ramping capability, making it less suitable for responding to rapid grid fluctuations.
Improving ramping capabilities is crucial for grid flexibility and reliability. Modern solutions include grid-forming inverters that allow wind and solar to provide frequency support, battery storage systems that offer instantaneous response, and demand response programs that dynamically adjust electricity consumption.

## Slide 8
8
8
Lecture 2.1 References
Song, J., Zhou, X., Zhou, Z., Wang, Y., Wang, Y., & Wang, X. (2023). Review of Low Inertia in Power Systems Caused by High Proportion of Renewable Energy Grid Integration. Energies, 16(16), 6042. https://doi.org/10.3390/en16166042
Ela, E., Milligan, M. and Kirby, B. (2011). Operating Reserves and Variable Generation, US National Renewable Energy Laboratory, Golden, Colorado. DOI: 102172/1023095
IRENA (2019), Innovation landscape brief: Flexibility in conventional power plants, International Renewable Energy Agency, Abu Dhabi.

## Slide 9
Chart: Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Electricity demand | 42 | 41 | 39 | 36 | 34 | 39 | 41 | 43 | 46 | 47 | 48 | 47 | 45 | 44 | 42 | 41 | 39 | 43 | 49 | 55 | 53 | 50 | 47 | 45
Generation | 42.5 | 41.5 | 39.5 | 36.5 | 34.5 | 39.5 | 41.5 | 43.5 | 46.5 | 47.5 | 48.5 | 47.5 | 45.5 | 44.5 | 42.5 | 41.5 | 39.5 | 43.5 | 49.5 | 52 | 53.5 | 50.5 | 47.5 | 45.5
9
2.2.1 Loss of load
2.2 Flexibility issues
The power system is unable to meet electricity demand due to insufficient generation or transmission capacity.
Loss of load can occur under different conditions, such as generation shortages, grid failures, and extreme climate events.
Generation < Electricity demand
Notes: Loss of Load occurs when the power system is unable to meet electricity demand due to insufficient generation or transmission capacity, leading to blackouts, brownouts, or forced load shedding. This situation can arise when electricity consumption exceeds the available supply, particularly during peak demand periods or unexpected system failures. Loss of load is a key reliability concern for grid operators, as it directly impacts consumers, industries, and critical infrastructure such as hospitals and transportation networks. A well-functioning power system is designed to minimize the risk of loss of load by ensuring adequate generation capacity and a resilient transmission network.
Several factors contribute to loss of load, ranging from generation shortages to grid failures and extreme weather conditions. Inadequate investment in power plants or delays in bringing new capacity online can lead to insufficient generation during peak hours, particularly in regions with growing electricity demand. Additionally, power systems that rely heavily on variable renewable energy (VRE), such as wind and solar, may face supply shortages when these resources underperform due to low wind speeds or reduced sunlight. Grid failures, including transmission line outages or equipment malfunctions, can also cause loss of load by preventing electricity from reaching consumers, even when sufficient generation exists. Furthermore, climate-related events, such as heatwaves, cold snaps, hurricanes, and droughts, can strain the power system by increasing demand and disrupting supply, making loss of load a growing concern in the face of global climate change.

## Slide 10
Chart: Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Electricity demand | 42 | 41 | 39 | 36 | 34 | 39 | 41 | 43 | 46 | 47 | 48 | 47 | 45 | 44 | 42 | 41 | 39 | 43 | 49 | 55 | 53 | 50 | 47 | 45
Generation | 42.5 | 41.5 | 39.5 | 36.5 | 34.5 | 39.5 | 41.5 | 43.5 | 46.5 | 47.5 | 52.5 | 49.5 | 45.5 | 44.5 | 42.5 | 41.5 | 39.5 | 43.5 | 49.5 | 55.5 | 53.5 | 50.5 | 47.5 | 45.5
10
2.2.2 Curtailment
2.2 Flexibility issues
The curtailed energy is the difference between the total available energy and actual dispatched production.
This is most commonly observed in solar and wind energy sources.
Generation > Electricity demand
Notes: Most energy practitioners are familiar with the curtailment of variable renewable energy (VRE) sources, such as wind and solar photovoltaics, which refers to a reduction in power generation compared to the total energy available from these resources. Curtailment represents the difference between the total potential energy and the actual energy produced. More broadly, it is the deliberate reduction of instantaneous power from supply or demand resources to help balance the electricity grid. This concept is commonly applied to supply-side resources, where output is intentionally reduced regardless of the technology, similar to a “dispatch down” instruction issued by system operators to decrease generation from any resource.
Curtailment occurs when the available wind and solar energy exceeds electricity demand while accounting for the operational constraints of other generators. In such cases, if there is no participation from demand-side resources, no expanded transmission capacity, no storage solutions, or no ability to export excess energy to neighboring systems, operators must curtail VRE output. While curtailment can sometimes be a cost-effective alternative to network expansion when integrating VRE, excessive curtailment diminishes the economic benefits of new wind and solar projects, given their low marginal costs. Additionally, it restricts the role of VRE in decarbonizing the power grid by limiting its overall contribution.
To mitigate curtailment and enhance the utilization of available VRE generation, solutions such as energy storage, demand-side management, and network expansion can be implemented. In summary, VRE curtailment typically occurs due to two main factors: (1) oversupply and system security concerns and (2) transmission congestion and local grid constraints.
A related concept is spillage, which refers to the unused energy potential of hydropower plants when excess water is discharged without being used for electricity generation. Spillage often occurs when reservoirs reach capacity and additional water must be released to prevent flooding, yet there is insufficient demand or generating capacity to convert it into electricity. While curtailment is an intentional grid management decision affecting primarily wind and solar power, spillage results from physical storage limitations in hydroelectric systems. Both curtailment and spillage highlight inefficiencies in power systems and the need for better storage solutions, transmission upgrades, and flexible demand management to fully utilize available energy resources.

## Slide 11
Chart: Hour
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Electricity demand | 22 | 24 | 23 | 26 | 67 | 65 | 63 | 28 | 29 | 31 | 34 | 36 | 33 | 32 | 31 | 28 | 37 | 69 | 75 | 72 | 68 | 62 | 55 | 51
11
2.2.3 Ramping capacity issues
2.2 Flexibility issues
Power plants or other resources cannot adjust their output quickly enough to maintain system balance.
Ramping capacity is required for shortages during peak demand periods or sudden renewable generation changes.
Ramps
Notes: As discussed in Lecture 1, ramping capacity refers to the ability of power generation units to increase or decrease their output in response to changes in electricity demand or supply. Ramping capacity issues arise when power plants or other resources cannot adjust their output quickly enough to maintain system balance, leading to operational challenges and potential reliability concerns. These issues have become more critical with the growing share of variable renewable energy (VRE), such as wind and solar, which introduce rapid fluctuations in power generation.
A key challenge with ramping capacity is insufficient flexibility in the generation mix. Traditional power plants, such as coal and nuclear, operate efficiently at constant output levels but have slow ramping capabilities, making it difficult for them to respond to sudden changes in demand or renewable generation. In contrast, gas-fired plants (especially SCGTs and some CCGTs), hydropower, and battery storage offer faster ramping capabilities and are often used to compensate for fluctuations in VRE output. However, if a system lacks sufficient fast-ramping resources, it may struggle to handle sudden drops in solar or wind generation or sharp increases in electricity demand, leading to frequency deviations, higher operational costs, or even load-shedding events.
Another significant issue is ramping shortages during peak demand periods or sudden renewable generation changes. For example, in the evening, when solar power generation rapidly declines while electricity demand rises (often referred to as the "duck curve" phenomenon as discussed in Lecture 1), power systems require a large amount of flexible capacity to ramp up quickly. If ramping capability is insufficient, system operators may need to curtail renewables, activate costly reserves, or even rely on emergency power measures to avoid disruptions. Solutions to mitigate ramping capacity issues include enhancing grid flexibility with energy storage, improving demand response programs, upgrading market mechanisms to incentivize flexible generation, and optimizing transmission infrastructure to distribute ramping needs more efficiently across regions.

## Slide 12
12
2.2.4 Reserves inadequacy
2.2 Flexibility issues
Lack of operating reserves to maintain reliability in case of sudden demand increases or unexpected generation losses.
Operating reserves involve multiple stages, each differing in reaction time and duration.
Source: Wikipedia (public domain)
Notes: Reserve inadequacy occurs when a power system does not have enough operating reserves to maintain reliability in case of sudden demand increases or unexpected generation losses. Operating reserves are extra generation capacities that can be quickly activated to balance supply and demand in real time. When these reserves are insufficient, the system becomes vulnerable to frequency instability, voltage fluctuations, load shedding, or even blackouts.
Reserve inadequacy can arise from several factors, including higher-than-expected demand, unplanned generator outages, extreme weather events, or the variability of renewable energy sources. Traditional power plants, such as coal and nuclear, provide stable but slow-reacting reserves, while gas turbines, hydroelectric plants, and battery storage offer faster response times. However, if there is not enough flexible capacity available to compensate for sudden power imbalances, the system operator may have to take emergency measures, such as importing electricity from neighboring grids or initiating demand-side reductions.
To address reserve inadequacy, system operators must enhance forecasting, improve demand response programs, deploy more energy storage, and design market mechanisms that incentivize flexible generation resources. Strengthening grid infrastructure and increasing regional interconnections can also help improve reserve adequacy by allowing power to be shared more efficiently across different areas.
During a loss of supply event, additional power must be quickly dispatched to stabilize the grid. As illustrated in the slide, this response involves multiple stages, each differing in reaction time and duration. Immediately after the supply loss, synchronous machines provide kinetic energy to the grid by slowing their rotational speeds, which in turn lowers the electrical frequency. This inertial response, inherent to synchronous generators and motors, helps slow the rate of frequency decline. In simple terms, the greater the system’s inertia, the more gradual the frequency drop. As frequency decreases, generators automatically react through governor control, while some loads also respond to help balance generation and demand at a frequency below the nominal level. To restore frequency, both spinning reserves—synchronous to the grid and operating below their maximum capacity—and non-spinning reserves—offline but capable of rapid synchronization—are deployed to compensate for the lost supply. Finally, replacement reserves, which have a slower response time, are activated to allow the initial reserves to be reset, ensuring the system is prepared for future disturbances. In the case of over-frequency events, though less common, a similar process occurs, but instead of increasing supply, generation is reduced to bring frequency back to its nominal level.

## Slide 13
13
2.2.5 Insufficient inertia
2.2 Flexibility issues
Insufficient inertia means not enough stored rotational energy in the system.
Options to mitigate this include grid-forming inverters, synthetic inertia from wind turbines, battery energy storage systems, and demand response programs.
Failed generator
Source: Modified from Ela et al. (2011)
Notes: As discussed in Lecture 1, inertia in power systems refers to the stored rotational energy in large synchronous generators (such as those in coal, nuclear, and hydro power plants) and some industrial motors. This inertia helps stabilize the grid by resisting sudden changes in frequency when there are power imbalances. When a generator or transmission line unexpectedly fails, inertia slows the rate at which frequency drops, giving the system time to activate reserves and restore balance. Insufficient inertia occurs when there is not enough stored rotational energy in the system, making it more vulnerable to rapid frequency deviations, instability, and even blackouts.
The shift toward renewable energy sources like wind and solar has significantly contributed to inertia challenges. Unlike traditional synchronous generators, wind turbines and solar PV systems are connected to the grid via power electronics (inverters) and do not inherently provide inertia. In power systems with a high share of inverter-based renewables, frequency disturbances can escalate much faster because there is less mechanical inertia to slow down frequency changes. This can lead to higher risks of grid instability, increased reliance on fast-response reserves, and potential system failures if corrective actions are not taken in time.
To mitigate the risks of insufficient inertia, system operators can adopt grid-forming inverters, synthetic inertia from wind turbines, battery energy storage systems, and demand response programs. Additionally, expanding regional interconnections allows grids with higher inertia to support those with lower inertia, improving overall stability. Some power markets also introduce ancillary service mechanisms that incentivize resources capable of providing synthetic inertia and fast frequency response.

## Slide 14
14
2.2.6 Grid congestion
2.2 Flexibility issues
This occurs when transmission lines reach their maximum capacity, preventing electricity (often VRE sources) from reaching demand centers.
Solutions like storage, demand response, and grid reinforcement help relieve congestion and enable more efficient, flexible operation.
Generation sites
Demand centers
Notes: Grid congestion occurs when the transmission network lacks sufficient capacity to transport electricity from where it is generated to where it is needed. This can result in situations where low-cost or renewable energy sources must be curtailed, not because of a lack of generation, but due to physical limitations in the grid infrastructure. Congestion is especially common in regions with high shares of variable renewable energy, such as wind or solar farms located far from major demand centers, leading to bottlenecks in power flow.
Grid congestion limits the power system’s ability to respond dynamically to changing supply and demand conditions, which is a core aspect of flexibility. When the grid is constrained, operators have fewer options to dispatch generation resources optimally or absorb fluctuations in variable renewable output. This not only increases operational costs by forcing reliance on more expensive or less efficient generation closer to load centers, but also reduces system resilience, as it restricts the ability to balance supply and demand across a broader geographic area.
To mitigate grid congestion and enhance system flexibility, several solutions can be pursued. First, investing in new transmission lines or reinforcing existing corridors can expand the physical capacity of the grid. Second, storage technologies and distributed energy resources can help relieve congestion by absorbing excess energy locally and discharging it when needed. Third, demand response programs can shift or reduce consumption in congested areas during peak periods. Lastly, better grid planning and digital tools such as advanced grid monitoring and congestion forecasting can improve real-time operation and long-term infrastructure planning.

## Slide 15
15
2.2.7 Flexibility solutions
2.2 Flexibility issues
Flexibility Issue | Flexibility sources |  |  |  |  | 
 | Fast-ramping generation | Storage technologies | Interconnectors and transmission | Demand response | Sector coupling | Gird-forming inverters
Ramping capacity issues | X | X |  | X |  | 
Loss of load |  | X | X |  | X | 
Inadequate reserves | X | X |  | X |  | 
Curtailment |  | X | X |  | X | 
Grid congestion |  | X | X |  |  | 
Insufficient inertia |  |  |  |  |  | X
Notes: As we will see in the next sections, there are several options to provide flexibility to the power systems. The table presents a clear mapping between key flexibility issues and the sources of flexibility that can address them. Each row identifies a challenge as described previously while each column represents a category of flexibility source, including fast-ramping generation, storage technologies, interconnectors, demand response, sector coupling, and grid-forming inverters. An “X” in a given cell indicates that the corresponding flexibility source is applicable to mitigate the identified issue.
From the table, it is evident that storage technologies and interconnectors are among the most versatile solutions, addressing multiple flexibility needs across various dimensions of system stress. For example, storage is marked as relevant for ramping issues, loss of load, inadequate reserves, and curtailment, while interconnectors help mitigate curtailment, congestion, and loss of load by facilitating cross-border balancing and capacity sharing. Demand response and sector coupling are also highlighted as important tools for increasing flexibility on the demand side, enabling load shifting and the integration of electricity with other sectors such as heating, cooling, and transport.

## Slide 16
16
Lecture 2.2 References
NREL. 2024. What Is Power System Curtailment?. https://www.nrel.gov/docs/fy25osti/90517.pdf
Ela, E., Milligan, M. and Kirby, B. (2011). Operating Reserves and Variable Generation, US National Renewable Energy Laboratory, Golden, Colorado. DOI: 102172/1023095

## Slide 17
17
2.3.1 Technical flexibility
2.3 Supply-side flexibility
Source: Modified from IRENA (2018)
Notes: Technical flexibility is closely linked to the physical structure of the power system. It refers to the combination of technologies that enable:
Supply to respond to rapid changes in net load,
Demand to adjust in response to fluctuations in supply,
Energy storage to balance supply and demand mismatches across all time scales, and
Grid infrastructure to efficiently deliver least-cost electricity to meet demand at any location and time within the power system.
The figure illustrates different technical strategies for enhancing power system flexibility as the share of variable renewable energy (VRE) increases. The x-axis represents the increasing penetration of VRE, such as wind and solar, while the y-axis represents the relative cost of each flexibility solution. The arrows highlight various approaches categorized into four types: supply-side flexibility (yellow), demand-side flexibility (dark blue), flexibility from storage (light blue), and grid infrastructure (medium blue). Lower-cost options, such as demand response and retrofitting existing thermal units, are positioned towards the bottom, whereas higher-cost solutions like sector coupling (hydrogen, heat pumps, and electric vehicles) and energy storage appear at the top.
At lower levels of VRE penetration, demand-side flexibility and improving existing thermal power plants provide cost-effective ways to balance supply and demand. Demand response, particularly in residential and industrial sectors, allows for shifting electricity consumption to better match renewable generation. Meanwhile, retrofitting existing thermal units by decreasing their minimum load, reducing startup times, and improving ramping capabilities enhances their ability to complement intermittent renewables. Grid infrastructure improvements, such as transmission expansion and distribution strengthening, further support system stability and facilitate the integration of renewables.
As VRE penetration increases, more advanced and higher-cost flexibility measures become necessary. Energy storage technologies, including batteries, pumped hydro, thermal storage, and electrofuel storage, help mitigate variability by storing excess renewable energy and discharging it when needed. Sector coupling, involving hydrogen production, heat pumps, and electric vehicles (EVs), plays a critical role in utilizing surplus renewable electricity across different sectors. Additionally, new flexible power plants and "X to power" solutions provide further reliability.

## Slide 18
Peak generators
Mid-merit generators
Baseload generators
18
2.3.2 Groups of generation technologies
2.3 Supply-side flexibility
Source: IRENA (2018)
Notes: Currently, dispatchable generators are the largest source of flexibility on the supply side. However, as demand gets less predictable, and more flexible along with the uptake of several flexibility alternatives, this concept could get less relevant in the future power systems. According to I.E.A., "A flexible generator is one with fast ramping capabilities, a low minimum operating level and fast start-up and shutdown times". Three major groups of generation technologies can be identified based on their ability to alter their output:
Baseload units usually have limited cycling capabilities and cannot ramp up or down their output quickly. Baseload technologies usually require a large upfront investment. However, they can produce large amounts of power at a relatively low operating cost. Therefore, they are used to supply the non-variable part of power demand. An example of a baseload unit is a nuclear plant.
Peak generators usually have opposite techno-economic characteristics; they require a lower upfront investment but higher operating cost. Peak generators have a very flexible operation and have the characteristics of rapid start-up and shut down, fast ramping capabilities, and low minimum operational level. Therefore they are suitable for fast response to short-term variability over peak hours and forecast errors. Peak generators usually have very low capacity factors and have a different business model compared to baseload units. Examples of peak generation units are open cycle gas turbines and internal combustion generators.
Mid-merit generators can be used either as baseload or peak load and usually have a slower response rate compared to peak generators. They can provide flexibility within an hour and are used for load following and supplying the intermediate demand. Examples of intermediate generators are combined-cycle gas turbines and hydropower.

## Slide 19
19
2.3.3 Increasing flexibility in thermal power plants
2.3 Supply-side flexibility
Key questions about the flexibility provided by dispatchable generation to the system:
What is installed capacity of each dispatchable technology? (MW)
How fast can each ramp up/down its output? (MW/minute)
How quickly can it start up/shut down?
What is the minimum stable output level?
What are the start-up costs and ramping costs?
Source: IRENA (2018)
Notes: There have been growing attempts to improve the flexibility provided by thermal generations as the V.R.E. sources are gradually becoming the mainstay of the power system. Modern designs of thermal generators offer improved performance, such as higher ramping rates and faster start-up, especially for coal and gas technologies.
Nuclear power plants have varying levels of flexibility, and some have the technical ability to ramp up or down relatively rapidly. According to I.E.A., some nuclear plants' operation data show that in the load-following mode, they can ramp up from 30% to 100% in one hour (and vice-versa). However, this capability may be constrained to contingency use for economic or security reasons.
In a system with a high share of V.R.E., limited curtailment of V.R.E. can also be a very cost-effective source of flexibility and provide down-regulation. Geographic dispersion of V.R.E. resources can also reduce the congestion on transmission and provide more flexibility to the system. In deregulated markets, flexibility is gradually becoming an important revenue source as generators should respond to price signals; therefore, flexibility gets remunerated. In regulated environments, increasing the flexibility of existing plants through retrofitting plans is gaining attention as a short to medium-term solution.
In summary, there are four key questions that should be answered to assess the flexibility provided by dispatchable generators:
• What is the installed capacity of each dispatchable technology?
• How fast can each unit ramp up or down its output?
• How quickly can it start up or shut down?
• What is the minimum stable output level?
• What are the start-up costs and ramping costs?

## Slide 20
20
2.3.4 Energy storage
2.3 Supply-side flexibility
Months
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Pumped Hydro CAES
Power to gas
Batteries
Flywheels
Source: IRENA (2020)
Key questions about the flexibility provided by energy storage to the system:
What is installed capacity of each storage type? (MW)
How fast it can be charged/discharged? (MW/minute)
What is the maximum energy storage capacity? (MWh)
Does the storage unit have the ability to provide inertia to the system?
Notes: The primary purpose of electricity storage is to shift electricity supply over time by storing electricity when its value is the lowest and discharging when its value is the highest. The attributed value of electricity storage in this context comes from reductions in the overall generation cost by avoiding V.R.E. curtailment, reducing thermal plants operation cycles, and preventing more expensive generators from running. Storage can facilitate high shares of V.R.E. by mitigating their impact on grid operations. We previously discussed that the impacts of V.R.E. vary over different time scales. Hence, to maximize their value for the power system, storage technologies should have appropriate technical characteristics across different time scales such as fast response time and ability to provide inertia.
At the shortest time scale (seconds), storage technologies such as pumped hydro and synchronous flywheels can provide inertia and reduce a system’s dependence on thermal generators for providing inertia. At a time scale of seconds to minutes, storage is mainly used for balancing and provision of operational reserves. Technologies such as pumped hydro, the power to gas, and state of the art long-duration batteries are used for balancing over more extended periods and between seasons.
In summary, there are four key questions that should be answered in order to assess the flexibility provided by an energy storage unit:
• What is the installed capacity of each storage type?
• How fast it can be charged and discharged?
• What is the maximum energy storage capacity?
• Can the storage unit provide inertia?

## Slide 21
21
2.3.5 Grid flexibility
2.3 Supply-side flexibility
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Interconnectors & Transmission
Months
Source: IRENA (2018)
Key questions about flexibility provided through interconnection/transmission in a region:
What is interconnection/transmission capacity to neighbouring regions/countries? (MW)
Is there a limit on the rate at which it can be operated? (MW / minute)
Does the connection enable sharing inertia to the system?
Notes: Grid flexibility through expanding interconnection and transmission lines allows the shared use of flexible resources to manage variability among connected regions. Therefore, while the storage balances supply and demand over time, transmission and interconnection balance that over space. Grid flexibility bridges supply-side and demand-side flexibility.
Therefore, low flexibility in the grid could become a bottleneck to the system flexibility. For example, in a system with high supply-side flexibility, the congestion in the grid could still limit integrating high shares of V.R.E. Furthermore, inertia between two systems can be shared through synchronous connections (via A.C.). For example, since the interconnection between Ireland and the UK is direct current (or D.C.), the two regions cannot share inertia.
The maximum flexibility capacity (power ramp) provided by an interconnection or transmission line is approximately equal to twice its rated capacity. This rated capacity is equal to the overall power ramping provided if the transmission line exporting at maximum capacity can switch to importing at maximum capacity.
Therefore, there are three key questions that should be answered in order to assess the flexibility provided by a transmission or interconnector line:
• What is interconnection and transmission capacity to neighbouring regions and countries?
• Is there a limit on the rate at which it can be operated?
• Does the connection enable sharing inertia to the system?

## Slide 22
22
2.3.6 Operational flexibility
2.3 Supply-side flexibility
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Pooling of resources
Intra-day market & Improved VRE forecasting
Co-optimised hydro-thermal unit commitment
Months
Source: IRENA (2018)
Examples of key questions about the flexibility provided by operation practices into the system:
Does the regulatory framework and market structure encourage the power exchange between regions?
Does the current market structure incentivize investment in the flexible generation?
Can the time step for planning the day ahead and intra-day market balancing be reduced?
Can improved VRE forecasts be incorporated into market planning?
Notes: The last source of flexibility is operational flexibility, which is about the regulatory framework and the market environment surrounding the power system. Operational flexibility includes investment free solutions for unlocking the system's flexibility by improving how the assets in the power system are operated. The market and regulatory frameworks act as an inhibitor to existing technical flexibility on the supply-side and demand-side. Centralized dispatching and building a market based on price merit to schedule electricity exchanges are examples of operation mechanisms that could facilitate investment and coordination to unlock the flexibility in the power system. A real-world example in this area is the European Commission’s Clean Energy Package which strongly supports market-based procurement of flexibility (more info on https://fsr.eui.eu/flexibility-mechanisms-what-is-it-about/).
Operation flexibility can also exist in different time scales to address different flexibility issues. In the medium to short-term, the use of modern forecast technologies and reducing the time step of day-ahead and intra-day market balancing are operational measures that can reduce the impact of V.R.E. uncertainty on the system. In the long-term, regulators can provide better long-term price signals to incentivize investment in flexible resources by increasing the time and space granularity of wholesale markets or restructuring the capacity market.
Therefore various questions should be answered to assess the potential for unlocking flexibility in the power system through operational measures such as:
•Does the regulatory framework and market structure incentivize the power exchange between regions?
•Does the market structure incentivize investment in the flexible generation?
•Can the time step for the day ahead planning and intra-day market balancing be reduced?
•Can improved V.R.E. forecasts be incorporated into market planning?

## Slide 23
23
23
Lecture 2.3 References
IRENA. 2018. “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA (2020a), “Electricity storage valuation framework: Assessing system value and ensuring project viability” (2020), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2020/Mar/Electricity-Storage-Valuation-Framework-2020

## Slide 24
24
2.4.1 Flexibility resources on the demand side
2.4 Demand-side flexibility
Seconds
Minutes
Hours
Days
Regulation
Balancing
Unit Commitment
Seasonal balancing
Load following
Aggregators providing demand-side flexibility
EVs
Power to heat
Power to gas
Industrial/Commercial demand response providing reserve
Months
Source: IRENA (2019)
Therefore, as with other resources, some key questions need to be answered to assess the technical capacity of flexibility resources on the demand side:
What is the size of the demand-side resource in terms of the total demand that can be curtailed or shifted? (MW)
When and how fast can the demand be curtailed/shifted? (MW / minute)
Is there a limit on the duration of curtailment/shift? (MWh)
Notes: Traditionally demand was considered inflexible in the power system, and the power system operators adjusted the supply to match the electricity demand. However, as the share of variable renewable sources is increasing, the supply-side is becoming less flexible. Therefore demand needs to become more flexible. Demand-side flexibility refers to shifting or curtailing consumer demand and implies transitioning to a system in which demand can be modified to better match electricity supply.
I.E.A. categorize demand-side flexibility resources as managed resources and responsive resources. Managed resources are consumers, usually industrial or commercial, that adjust their electricity consumption based on long-term direct control agreements. These resources are contracted in advance by a system operator to reduce their consumption for a certain number of hours per year. This implies that a certain proportion of the consumer's demand can be postponed without economic hardship.
A responsive resource is the proportion of consumer's demand that the system can rely on to respond dynamically, through price signals, to scarcity or surplus of electricity by decreasing or increasing consumption.
Therefore three key questions need to be answered to assess the technical capacity of flexible resources on the demand side:
• What is the size of the demand-side resource in terms of the total demand that can be curtailed or shifted?
• When and how fast can the demand be curtailed or shifted?
• Is there a limit on the duration of curtailment or shift?

## Slide 25
25
2.4.2 Demand response (DR)
2.4 Demand-side flexibility
Demand response
Price-based programmes
Incentive-based programmes
Demand response (DR) provides incentives to shift or reduce electricity demand in wholesale and ancillary power markets, helping to balance the grid.
DR programs are generally categorized into two main types: incentive-based and price-based mechanisms.
Notes: The U.S. Department of Energy (DoE) defines demand response (DR) as "changes in electric usage by end-use customers from their normal consumption patterns in response to changes in the price of electricity over time, or to incentive payments designed to induce lower electricity use at times of high wholesale market prices or when system reliability is jeopardized."
Advancements in smart grid technologies, including Information and Communications Technology (ICT), intelligent energy management systems (EMSs) at end-user premises, and smart grid-compatible advanced metering infrastructure (AMI), have facilitated the adoption of DR strategies by independent system operators (ISOs) in leading markets worldwide.
DR programs are typically categorized into two types:
Price-based DR (implicit demand response): Consumers are encouraged to shift electricity consumption in response to price signals and tariffs.
Incentive-based DR (explicit demand response): Consumers receive direct payments for reducing or shifting demand as part of a demand-side response program.

## Slide 26
26
2.4.3 Demand aggregators
2.4 Demand-side flexibility
Source: IRENA (2019)
Aggregators enhance demand response by contracting with diverse end-users, controlling their assets, and forming larger demand blocks that can participate in electricity markets.
Time-of-use pricing incentivizes consumers to shift their demand, reducing peak consumption and supporting variable renewable energy integration by aligning demand with supply conditions.
Notes: Consumers participating in demand response and management have various sizes ranging from individual residential and commercial consumers to large industrial consumers. They are located in different zones on the power network. One of the key challenges of demand response is to form a coordination of loads of various size to meet the required response rates or capacity reduction in different nodes.
One way of increasing responsiveness is to aggregate demand from end-users of various sizes and form a larger demand block. Aggregators are companies that contract with different end-users and distributed energy resource owners to control their assets on their behalf. Aggregators then act as a participant in the electricity and ancillary services market by controlling assets belonging to end-users and aggregate them to operate as a single demand-side response block. To do so, aggregators could use smart metering or smart appliances that can respond automatically to price signals from the system.
Another measure to facilitate demand-response is adopting the time-of-use rates that change based on power market prices to provide incentives for reducing consumption during peak hours. Time-of-use pricing can also support V.R.E. by increasing demand during over-generation and adjusting demand to reduce netload ramps. As a result, the need for conventional peak capacity in the power system and the cycling of the thermal generations reduces. As in the case of other resources, there is a limit on the maximum demand response capacity. The economic and technical effectiveness of demand response is at a maximum during the early stages and decreases as this capacity increases

## Slide 27
27
2.4.4 Sector coupling: Power to heat
2.4 Demand-side flexibility
Centralized electricity infrastructure
Decentralized electricity infrastructure
Thermal and renewable power plants
Electric vehicles
Residential PV and storage
Electricity network
Heat network
Heat plants and CHP plants
Centralized heat storage
Centralized heat pumps
Centralized electric boilers
District heating
Industrial heating
Heat supply
Heat demand
Direct electric heating
Electric thermal storage
Decentral heat pumps
Decentral
electric boilers
P2H
P2H
P2H
P2H
P2H
P2H
Source: Ramsebner et al. (2021)
Notes: In the context of power system flexibility, sector coupling refers to the integration of the electricity sector with other energy-consuming sectors, such as heating, transport, and industry, to improve the overall flexibility and efficiency of the energy system. We’ll discuss several options of sector coupling in this and following sections.
Power-to-Heat (P2H) is a sector coupling strategy that converts electricity into thermal energy for use in heating applications. It enables the integration of surplus renewable energy, especially from wind and solar power, into the heating sector, reducing reliance on fossil fuels for heat production. By using electric boilers, heat pumps, or resistance heaters, P2H systems can store excess electricity as heat, which can be used for district heating, industrial processes, or domestic heating systems as illustrated in the figure. This approach helps balance electricity supply and demand by absorbing excess renewable generation when supply exceeds demand, thereby reducing curtailment and improving grid flexibility.
A key advantage of P2H is its ability to enhance energy efficiency and decarbonize heat production. Traditional heating systems rely on coal, gas, or oil, whereas P2H enables a shift to low-carbon electricity. Large-scale applications, such as district heating networks, can store heat in thermal storage systems, ensuring a continuous and stable heat supply even when electricity availability fluctuates. Additionally, industrial sectors requiring high-temperature heat can benefit from P2H, replacing fossil fuel-based heat sources with renewable electricity.
In power systems with high shares of variable renewable energy, P2H can function as a flexibility tool by dynamically adjusting heat production in response to electricity market conditions. For example, during periods of high wind or solar generation, P2H units can increase heat production, effectively absorbing excess electricity and preventing grid congestion. Conversely, during times of low renewable generation, P2H systems can reduce electricity consumption and rely on stored heat. This integration of electricity and heat sectors contributes to a more resilient, efficient, and low-carbon energy system.

## Slide 28
28
2.4.5 Sector coupling: Power to Gas
2.4 Demand-side flexibility
Gas network
Gas storage
H2O
CO2
CH4
H2
Renewable electricity
Electrolysis
Methanation
Blending
Final end-uses
Industry
Transport
Heating
Power generation
Notes: Power-to-Gas (P2G) is a sector coupling strategy that converts surplus electricity, especially from renewable sources like wind and solar, into gaseous fuels such as hydrogen or synthetic methane. This process allows excess renewable energy to be stored and used in sectors that are traditionally reliant on fossil fuels, including industry, heating, and transport. P2G enhances the flexibility of power systems by absorbing surplus electricity when renewable generation exceeds demand and feeding that energy back into the system when needed.
The P2G process consists of two main steps: electrolysis and (optionally) methanation as illustrated in the figure. In electrolysis, electricity is used to split water (H₂O) into hydrogen (H₂) and oxygen (O₂). This hydrogen can then be used directly in fuel cells, industrial applications, or as a transportation fuel. Alternatively, through a second step called methanation, hydrogen can be combined with CO₂ to produce synthetic methane (CH₄), which is chemically identical to natural gas and can be injected into existing gas grids, stored for long periods, or used in gas power plants.
P2G plays a crucial role in decarbonization and energy system flexibility. It enables the long-term storage of renewable energy, which is especially useful for managing seasonal variations in wind and solar generation. Additionally, hydrogen and synthetic methane can replace fossil fuels in hard-to-electrify sectors such as heavy industry, long-haul transport, and high-temperature heat production. By integrating the power, gas, and transport sectors, P2G reduces curtailment of renewable electricity, enhances grid stability, and supports deep decarbonization across multiple sectors.

## Slide 29
29
2.4.6 Sector coupling: Power to Liquids
2.4 Demand-side flexibility
Hydrocarbon network
H2O
CO2
Synthetic hydrocarbons
H2
Renewable electricity
Electrolysis
Chemical synthesis and fuel processing
Final end-uses
Industry
Transport
Heating
Notes: Power-to-Liquids (P2L) is a sector coupling technology that converts electricity—preferably from renewable sources—into liquid fuels such as synthetic diesel, gasoline, methanol, or jet fuel. This process enables the use of surplus renewable energy to produce carbon-neutral fuels that can replace fossil-based liquid fuels in aviation, shipping, heavy transport, and chemical industries. P2L plays a crucial role in decarbonizing sectors that are difficult to electrify, offering an alternative to conventional petroleum-derived fuels while improving power system flexibility.
The P2L process involves two main steps: electrolysis and fuel synthesis as illustrated in the figure. In the first step, electrolysis uses electricity to split water into hydrogen (H₂) and oxygen (O₂). The hydrogen is then combined with captured CO₂ through Fischer-Tropsch synthesis or methanol production to create synthetic hydrocarbons. These synthetic fuels can be stored, transported, and used in existing fuel infrastructure, making them a practical alternative to fossil fuels without requiring major modifications to current vehicles, aircraft, or industrial processes.
By converting excess renewable electricity into liquid fuels, P2L helps reduce curtailment of wind and solar energy while providing a long-term storage solution for renewable power. Unlike batteries or hydrogen, liquid fuels are energy-dense and easy to store and transport, making them especially valuable for sectors requiring high energy density and long-range capabilities. P2L is an essential technology for achieving carbon neutrality in transportation and industry while strengthening the integration of renewable energy into the overall energy system.

## Slide 30
30
2.4.7 Sector coupling: Electric vehicles
2.4 Demand-side flexibility
Electric vehicles
V2G Unit
Consumers
Grid
Vehicle-to-grid (V2G) scheme
Notes: Electric vehicles (EVs) play a key role in sector coupling by integrating the power and transport sectors, enabling greater flexibility in energy systems. By using electricity instead of fossil fuels, EVs help reduce emissions in transportation while providing opportunities for grid balancing and renewable energy integration. When charged during periods of high renewable generation—such as midday solar peaks or windy nights—EVs help absorb excess electricity, reducing curtailment and improving the utilization of clean energy. Additionally, smart charging technologies allow EVs to charge when electricity prices are low or when there is a surplus of renewable energy.
Beyond simply consuming electricity, EVs can actively support the grid through vehicle-to-grid (V2G) technology, where they function as distributed storage units. In a V2G system, EV batteries can store electricity when demand is low and feed it back into the grid when demand is high, helping to stabilize frequency and balance supply and demand. This flexibility is particularly valuable as power systems transition to high shares of variable renewable energy (VRE), such as wind and solar, which fluctuate based on weather conditions. Large-scale adoption of V2G technology could significantly reduce the need for stationary energy storage and backup power plants.
EVs also contribute to sector coupling in heating and industry through vehicle-to-home (V2H) and vehicle-to-building (V2B) applications. EVs can supply power to homes or buildings during peak hours, reducing stress on the grid and lowering electricity costs for consumers. Moreover, as battery technology improves, second-life EV batteries can be repurposed for stationary energy storage, extending their usefulness beyond their automotive lifespan. By linking transportation, electricity, and even heating sectors, EVs serve as a key enabler of a more flexible, resilient, and decarbonized energy system.

## Slide 31
31
Lecture 2.4 References
IRENA. 2018. “Power system flexibility for the energy transition, Part I: Overview for policy makers”, 2018, International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2018/Nov/Power-system-flexibility-for-the-energy-transition
IRENA. 2019, “Demand-side flexibility for power sector transformation” (2019), International Renewable Energy Agency, Abu Dhabi, https://www.irena.org/publications/2019/Dec/Demand-side-flexibility-for-power-sector-transformation
Nikolaos G. Paterakis, Ozan Erdinç, João P.S. Catalão, An overview of Demand Response: Key-elements and international experience, Renewable and Sustainable Energy Reviews,
Volume 69, 2017, Pages 871-891, ISSN 1364-0321, https://doi.org/10.1016/j.rser.2016.11.167
Ramsebner, J., Haas, R., Ajanovic, A., & Wietschel, M. (2021). The sector coupling concept: A critical review. In Wiley Interdisciplinary Reviews: Energy and Environment (Vol. 10, Issue 4). John Wiley and Sons Ltd. https://doi.org/10.1002/wene.396

## Slide 32: Thank you
www.climatecompatiblegrowth.com