## Slide 1
Assessing power system flexibility with IRENA FlexTool
LECTURE 4
FLEXTOOL ASSESSMENT STUDIES

## Slide 2
2
Learning Outcomes
By the end of this lecture, you will be able to:
ILO1: Overview the role of FlexTool as planning tool for flexibility assessments.
ILO2: Understand the main aspects involved in designing a flexibility assessment with FlexTool.
ILO3: Investigate the flexibility of an example case study.
ILO4: Understand the differences between different scenarios.

## Slide 3
3
4.1.1 Flexibility assessment tools
4.1 Overview
Tier 1 tools mainly provide a qualitative comparison of different power systems and, therefore, do not require a lot of data.
Tier 2 tools do a flexibility sufficiency check without performing full power system optimization. These tools are mainly aimed at screening the potential flexibility issues, using time series and dispatch data from an external tool.
Tier 3 tools are based on unit commitment and dispatch models and are sometimes combined with capacity planning models. Tier 3 models are complex and require a lot of data.
The IRENA FlexTool is a Tier 3 model and analyses system operations and flexibility of a system over one year horizon.
Notes: There are various tools for Flexibility assessment using different methods and with different levels of complexity. IRENA categorises different approaches for flexibility assessment into three categories of assessment tools, based on their complexity and their level of details:
• Tier 1 tools mainly provide a qualitative comparison of different power systems and, therefore, do not require a lot of data.
• Tier 2 tools do a flexibility sufficiency check without performing complete power system optimization. Tier 2 tools are mainly aimed at screening the potential flexibility issues using time series and dispatch data from an external tool.
• Tier 3 tools are based on unit commitment and dispatch models and are sometimes combined with capacity planning models.
These models provide a detailed picture of the power system operation and evolution in different scenarios and provide a solid foundation for flexibility assessment. However, Tier 3 models are complex and require a lot of data. In this course, we use IRENA FlexTool for the assessment of flexibility in a power system. The FlexTool is a Tier 3 model and analyses system operations and flexibility of a system over one year horizon. The FlexTool is data-driven and uses a general unit commitment model structure; therefore, the input data have a major role in specifying what the model does.

## Slide 4
4
4.1.2 FlexTool in the planning process
4.1 Overview
Grid studies
(Power Factory, PSS/E)
Optimal capacity expansion
System operation
1 second
1 hour
1 year
10 years
50 years
Dispatch models
(PLEXOS-ST, SDDP)
Capacity expansion models
(PLEXOS-LT, Opt-Gen)
Energy planning models
(OSeMOSYS, MESSAGE, TIMES)
Flextool dispatch
Flextool expansion
Time horizon analyzed
Source: IRENA (2019)
Notes: This figure illustrates the role of the IRENA FlexTool within the broader power system planning process, highlighting its applicability across different time horizons and planning objectives. The horizontal axis represents the time horizon analysed, ranging from real-time operational scales of seconds to long-term strategic horizons of 50 years. The vertical axis distinguishes between two main areas of analysis: optimal capacity expansion, which focuses on determining the most cost-effective investment pathways for generation and network infrastructure, and system operation, which deals with the efficient short- to medium-term dispatch and balancing of existing assets.
In terms of optimal capacity expansion, the figure shows that FlexTool can be used for medium- to long-term planning in timesteps of one year. It complements more specialised capacity expansion models (such as PLEXOS-LT and OptGen) and energy planning models (like MESSAGE, TIMES or OSeMOSYS), which typically address very long horizons, often several decades.
From the system operation perspective, FlexTool also offers a dispatch functionality, complementing more detailed dispatch models such as PLEXOS-ST and SDDP. While grid studies (e.g., Power Factory, PSS/E²) focus on second-to-hour operational timescales and network-specific performance, FlexTool dispatch can cover horizons from hours to years, allowing planners to evaluate how flexibility resources interact with the system under different operational scenarios. This dual capability, supporting both expansion and dispatch analysis, makes FlexTool a versatile instrument for linking short-term operational insights with long-term strategic planning.

## Slide 5
5
4.1.3 FlexTool input data requirements
4.1 Overview
System data (annual, each node)
Demand, imports, losses and capacity margin
Electricity transmisión (each node)
Transmission and interconnection capacities
Data of generation and storage capacity (each node)
Installed capacity., technical data of generators and storage, hydro reservoir capacities
Time-series data (8760 hourly values, each node)
Electricity demand, hydro inflows, wind and solar photovoltaic generation, reserves profiles, demand from other sectors (e.g., heat)
Fuel data
Fuel price and emission rate
Notes: This table summarises the key data requirements for running IRENA’s FlexTool, organised into different categories that capture the essential characteristics of a power system. At the system level, annual data per node is needed to describe overall demand, imports, losses, and the capacity margin. This provides the baseline understanding of the system’s energy balance and its reliability standards. Without this foundational information, it would be impossible to determine how the system meets its annual energy needs or how much reserve capacity is necessary to ensure security of supply.
Transmission-related inputs are also critical, as FlexTool requires information on the transmission and interconnection capacities for each node. These parameters determine the ability of different regions or zones to exchange electricity, which directly affects flexibility assessments. Similarly, generation and storage capacity data for each node must be provided, including installed capacity, technical specifications of generators, and the capacities of hydro reservoirs. This ensures that the model can accurately simulate the technical limits and operational characteristics of the generation fleet.
In addition to static capacity data, FlexTool relies heavily on time-series inputs to represent hourly variations throughout the year (8,760 hourly values per node). These include demand profiles, hydro inflows, wind and solar generation patterns, reserves profiles, and demand from other sectors such as heat. This high-resolution temporal data is essential for capturing the variability and intermittency of renewable energy sources. Finally, fuel-related inputs, including prices and emission rates, are required to evaluate the economic and environmental performance of different dispatch and investment options.

## Slide 6
6
4.1.4 FlexTool model outputs
4.1 Overview
Flexibility indicators | 
Loss of load (TWh and %) | VRE curtailment (TWh and %)
Reserves shortage (MW) | Capacity inadequacy (MW)
Spillage (TWh) | 
Dispatch per generator and per node | 
Transmission between nodes (and utilization factor of lines) | 
Costs | 
OPEX | CAPEX
Fuel costs | Generation investments
Costs of carbon dioxide emissions | Transmission investments
Operation and maintenance costs | Storage investments
Cost of loss of load | Sector coupling (e.g., heat pumps)
Cost of curtailment | 
Electricity price per node (marginal price) | 
Ramping information (one-hour and four-hour ramps) | 
Investments (invested transmission, generation, storage or sector coupling capacity) | 
Other (e.g., dispatch and costs from other energy sectors) | 
Notes: This table outlines the range of outputs that IRENA’s FlexTool can generate after running simulations, which are grouped into different categories to capture the technical, economic, and operational performance of the power system. One key set of outputs are flexibility indicators, which measure the system’s ability to meet demand and integrate variable renewable energy (VRE). These include loss of load (in TWh and percentage), reserve shortages, and capacity inadequacy (in MW), which point to potential reliability issues. Other indicators track VRE curtailment and spillage, both in energy terms (TWh) and percentages, providing insights into how well renewable resources are being utilised.
Another group of results focuses on operational performance and transmission flows. FlexTool provides detailed dispatch information per generator and per node, showing how each unit operates over time. It also reports electricity transmission between nodes, along with the utilisation factor of transmission lines, which is crucial for identifying potential congestion or underutilisation of infrastructure. Additionally, ramping information for one-hour and four-hour periods is provided, helping assess the system’s ability to respond to rapid changes in demand or renewable generation. This operational detail is complemented by marginal electricity prices per node, which reflect the cost of supplying the next unit of electricity at different locations.
Finally, the tool produces comprehensive cost-related outputs. These are split into operational expenditures (OPEX) such as fuel costs, carbon dioxide emissions costs, operation and maintenance expenses, and the costs of loss of load or curtailment, and capital expenditures (CAPEX) related to investments in generation, transmission, storage, and sector coupling technologies. FlexTool also records the value of already-invested infrastructure and can capture other relevant outputs, such as dispatch and costs from other energy sectors.

## Slide 7
7
Lecture 4.1 References
IRENA. 2019. IRENA FlexTool Summary of Methodology. International Renewable Energy Agency, Abu Dhabi.

## Slide 8
8
4.2.1 Flexibility study objectives
4.2 Designing a flexibility assessment
Source: IRENA (2019)
Notes: This figure outlines the three main objectives of studies conducted with the IRENA FlexTool, organised into primary, secondary, and tertiary goals. The primary objective is to assess the flexibility of capacity expansion plans. This involves identifying potential flexibility shortages in national electricity plans, examining system operations under non-average conditions such as dry years, and using capacity expansion plans from national authorities or IRENA’s REmap as a starting point. The focus here is on ensuring that planned expansions can handle variability and maintain reliability over time.
The secondary objective is to determine cost-efficient additional investments to address flexibility shortages. This means identifying the least-cost mix of solutions, covering generation, transmission, storage, and sector coupling, that can resolve identified gaps. The analysis also includes evaluating further investments that could minimise the total system cost, considering both capital expenditures (CAPEX) and operational expenditures (OPEX). This stage ensures that flexibility improvements are achieved without imposing unnecessary financial burdens on the system.
The tertiary objective looks at accommodating higher shares of variable renewable energy (VRE) by running sensitivity analyses. This helps assess the impacts of additional VRE deployment on system flexibility, identifying the threshold beyond which shortages begin to appear. Once this threshold is known, solutions can be developed to address these challenges. This step is particularly valuable for countries aiming for ambitious renewable targets, as it clarifies both the opportunities and the operational constraints associated with high VRE penetration.

## Slide 9
9
4.2.2 Flexibility enablers
4.2 Designing a flexibility assessment
Enabler | Units
Interconnected capacity vs. average demand | -
Generator ramping capabilities | MW/min
Matching of demand with VRE generation | %
Hydro inflow stability | %
Strength of internal grid | -
Storage vs. annual demand | %
Geographical dispersión of VRE generation and demand | -
VRE vs. mínimum demand | -
Notes: This table presents key flexibility enablers that determine how effectively a specific power system can adapt to changes in supply and demand, particularly when integrating variable renewable energy (VRE) sources. Indicators such as interconnection capacity versus average demand highlight the role of cross-border electricity exchanges, showing the ratio between interconnection capacity with neighbouring systems and the average electricity demand. Generator ramping capabilities, measured in MW per minute, reflect how quickly dispatchable generation can adjust output to balance fluctuations, assuming all units are operational. Another indicator, matching of demand with VRE generation, shows the correlation between demand patterns and renewable output, which is critical for reducing curtailment and improving utilisation.
Other enablers focus on resource stability and grid infrastructure. Hydro inflow stability, expressed as a percentage, measures the variability of historical hydro inflows, which can affect the reliability of hydro-based flexibility. The strength of the internal grid assesses the robustness and capacity of the national transmission network to handle power flows efficiently, avoiding bottlenecks that could limit flexibility. Storage versus annual demand quantifies the available storage capacity, including hydro reservoirs, relative to total yearly demand, indicating how much excess generation can be absorbed and shifted in time.
Finally, spatial and operational matching between generation and demand is addressed through geographical dispersion of VRE generation and demand, which shows the degree of alignment between where renewable energy is produced and where it is consumed. The VRE versus minimum demand indicator compares installed renewable capacity to the system’s lowest demand levels, signalling the potential for overgeneration and curtailment, especially if storage is insufficient. A higher ratio implies greater flexibility challenges, making this metric particularly important for planning storage capacity and demand-side management measures.

## Slide 10
10
4.2.3 FlexTool flexibility indicators
4.2 Designing a flexibility assessment
Indicator | Units | Description
Curtailment | GWh and MW | Occurs when VRE output has to be reduced because of the inflexibility of the system or because VRE generation exceeds the demand.
Loss of load | GWh and MW | Occurs when supply cannot match demand, and part of the electricity demand must go unserved (e.g., so-called load shedding).
Spillage | GWh and MW | Occurs when water inflow exceeds the amount that can be used by hydropower generators and reservoirs are already full.
Reserve inadequacy | GWh and MW | Occurs when the reserve requirement cannot be met.
Notes: The IRENA FlexTool provides a summary of potential flexibility and grid issues in the “summary” sheet of each results Excel file. This overview includes the following categories:
Loss of load (MW): Occurs when supply is insufficient to meet demand, resulting in unserved energy. The tool reports the maximum loss of load observed in a single period.
Reserve inadequacy (max MW): Arises when reserve requirements cannot be fulfilled. The tool displays the maximum shortfall in reserves during a single period.
Curtailment (max MW): Happens when variable renewable energy (VRE) output must be reduced due to system inflexibility or because VRE generation exceeds demand. The tool shows the highest curtailment recorded in a single period.
Curtailment (TWh): Similar to the previous indicator, but measured as the total curtailed energy over an entire year.
Capacity inadequacy (max MW): Occurs when installed capacity fails to meet the required capacity margin. The tool reports the largest capacity shortfall recorded in a single period.
Spill (TWh): Takes place when water inflows exceed what hydropower plants can utilise once reservoirs are full. The tool presents the total annual energy spilled.
All these events are permitted within the model’s optimisation process; however, they incur penalty costs as specified in the input data. While the FlexTool seeks to minimise these costs, limitations in system capacity or flexibility may still result in their occurrence within the cost-optimal solution.

## Slide 11
11
4.2.4 Resolving flexibility issues with FlexTool
4.2 Designing a flexibility assessment
Source: IRENA (2019)
Notes: This figure presents a quick decision-making guide for identifying and resolving flexibility issues using the IRENA FlexTool. The process starts with running the tool and reviewing the flexibility indicators in the results file. If all indicators are zero, it means there are no significant flexibility concerns, and the system operates at minimum total cost without reliability or integration issues. However, if any indicators show problems such as loss of load, reserve shortage, curtailment, or spillage, we should determine the nature of the problem and the most suitable solution.
When the issue is related to loss of load or reserve shortage, the user should check whether it is an adequacy issue. This occurs when annual generation is insufficient to meet annual demand, and there is no transmission congestion. In such cases, the recommended solution is to invest in additional generation capacity. Alternatively, if the problem is not purely adequacy-related but still involves flexibility constraints, the user is advised to consider a least-cost combination of flexibility solutions, which could include generation, transmission, storage, and sector coupling measures.
In cases where the main issue is curtailment or spill, the guide suggests checking whether there is excess variable renewable energy (VRE) generation, meaning that at certain times, renewable output exceeds demand, and whether the system has already undergone least-cost optimisation. If these conditions are met, the recommendation is to consider sector coupling strategies, such as using electricity for heat pumps or other demand-increasing applications, to absorb excess generation.

## Slide 12
12
4.2.5 Stakeholders and engagement
4.2 Designing a flexibility assessment
Initial discussions with the country to confirm interest in conducting a flexibility assessment with IRENA.
Stakeholder engagement to ensure study feasibility, relevance, credibility, and national applicability.
Key participants include IRENA focal point, utility companies, TSOs, ministries, and other decision makers.
IRENA invitation letter sent to formally launch the flexibility assessment process.
Notes: The application of the FlexTool in a country generally begins with preliminary discussions, during which the country expresses its interest in collaborating with IRENA on a flexibility assessment. These discussions, along with the case studies, involve the participation of relevant stakeholders to ensure the study’s feasibility, as well as the relevance, credibility, and applicability of its results for national purposes. Key participants include the IRENA focal point, responsible for identifying agencies or ministries that can provide the necessary data, and decision makers, such as utility companies, transmission system operators (TSOs), and government ministries, who can review and apply the findings.
Following these initial exchanges, IRENA issues an official invitation letter to the country to formally launch the flexibility assessment. From that point, collaboration begins with the designated focal point for data collection and analysis, who may or may not be the same individual or entity involved in the initial engagement process.

## Slide 13
13
13
Lecture 4.2 References
IRENA. 2019. IRENA FlexTool Summary of Methodology. International Renewable Energy Agency, Abu Dhabi.

## Slide 14
14
4.3.1 Thailand
4.3 Example case study
Main challenges of the Thai power system and FlexTool analysis done
Two scenarios regarding the future generation mix in 2036 are considered:
  A Reference scenario based on the Alternative Energy Development Plan, with insights from the Power Development Plan.
  The REmap scenario based on the Thailand Renewable Energy Outlook.
The REmap scenario considers higher renewable deployment and lower generation capacity.
Source: IRENA (2019)
Notes: In this lecture, we will explore an example case study of Thailand. The FlexTool engagement process for Thailand started with a formal invitation for the International Renewable Energy Agency (or IRENA) to act as the focal point entity for Thailand, the Ministry of Energy, and more specifically the Department of Alternative Energy Development and Efficiency.
This analysis helped to assess grid capacity to integrate more renewables, along with the economic impact of these renewables. The scenarios considered the future generation mix in 2036, with two specific scenarios: the reference scenario and the REmap scenario. The REmap scenario considers higher renewables deployment and lowers thermal generation capacity.
The Figure shows the main challenges identified before starting the assessment, as well as the relevant analysis, that was undertaken to cope with these challenges.
Firstly, there was limited experience in operating systems with high shares of variable renewable energy or VRE. Secondly, there was weak interconnection with other countries, and finally, the peak load of Thailand occurs after sunset.
The analysis undertaken simulates different VRE penetration scenarios (the reference scenario and REmap), as well as an assessment of the optimal power-generation capacity mix (including storage). Finally, the long-term planning for possible increases in VRE share, mostly from photovoltaics was analysed.

## Slide 15
15
4.3.2 Grid Analysis
4.3 Example case study
Connections with neighbouring countries:
  Long-term contracts with hydropower operators in Laos.
  Plans to expand hydropower in Laos and Myanmar.
  Otherwise weak connections.
Internal grid:
  Long country with uneven demand and production.
  Hydropower at north.
  Bangkok consumes much more than it produces.
  Not enough regional data available.
Modelling decisions:
  Model Thailand as a single node (main thing to improve).
Sketch of thailand’s transmission network
Source: IRENA (2019)
Notes: Firstly, we will analyse Thailand’s electricity grid.
Thailand has connections with Myanmar, with long-term contracts with hydropower operators there. However, there are plans to expand hydropower in both Laos and Myanmar. Otherwise, there are weak connections between neighbouring countries.
In terms of the internal grid, Thailand is a long country with uneven demand and production. For example, Bangkok consumes a lot more electricity than it produces, and there are large hydro facilities in the North of the country. However, not enough regional data are available for Thailand’s internal grid.
Several modelling decisions were made in this case study. For example, Thailand was modelled as a single node, which can be improved upon in future studies. The case study also includes contracted hydropower plants in Laos and Myanmar as part of the Thailand model.

## Slide 16
16
4.3.3 Capacity expansion scenarios
4.3 Example case study
Fast growth in electricity demand.
Current capacity expansion plans (“reference”):
  Meet demand by adding fossil fuel generation capacity.
  Invest relatively small share in wind and solar.
  Build several GW of pumped hydro capacity.
In one node model:
  No capacity adequacy issues expected (strong capacity balance).
  No ramping capacity issues expected (hydro reservoirs and natural gas).
  No curtailment expected (low VRE share).
  But could additional VRE capacity be cheaper than fossil fuel-based generation?
Expected evolution of Thailand’s generation capacity mix, 2015–2036
Source: IRENA (2019)
Notes: In this slide, we will explore the capacity expansion scenarios.
Annual electricity demand is expected to grow by 70% from 2015 to 2036 according to E. GAT and the Ministry of Energy.
It is expected that this rapid increase in electricity demand is met by the addition of fossil fuel generation capacity. A relatively small amount of share of wind and solar is expected, with several gigawatts of pumped hydro capacity to be built.
In the one node model, no capacity adequacy issues are expected, due to a strong capacity balance. There are not expected to be any capacity issues due to the presence of hydro reservoirs and natural gas. No curtailment is expected due to the low share of variable renewable energy (or V.R.E.) and the presence of hydro reservoirs and pumped hydro. However, a question that can be asked is, would additional variable renewable energy capacity be cheaper than fossil fuel-based generation?

## Slide 17
17
4.3.4 Lessons from operation practices
4.3 Example case study
Thailand’s peak electricity demand is after sunset.
  Solar PV cannot contribute directly to peak power.
  Storage is needed → Thailand has decided to invest in reservoir hydro and pumped hydro.
Hydro inflow variance between years can cause some issues.
  The variations between years are not exceptionally large, but dry years need to be simulated.
Geographical dispersion of VRE cannot be analysed with a one node model.
Strength of internal grid cannot be analysed with a one node model.
Thailand has data in 30-minute intervals, and the model was built with 30-minute time steps to pay additional attention to ramp rates.
Notes: In this slide, we review some lessons from operation practices.
A large factor in understanding the flexibility of Thailand is that its peak electricity demand is after the sunset. Therefore solar photovoltaics cannot contribute directly to peak power. This means that storage is needed. To this end, Thailand has decided to invest in both reservoir and pumped hydro. This can be used to meet the peaks in demand and lulls in supply from variable renewable energy.
A second factor which deserves attention is the hydro inflow variance. The variations between years in hydro inflow are not exceptionally large, but especially dry years do need to be simulated within FlexTool.
Another factor is that the geographical dispersion of variable renewable energy cannot be analysed with a single node model. Therefore, if we were to assess the effects of different weather conditions at different locations within Thailand more nodes would be required. Similarly, the strength of the internal grid cannot be analysed with a single node model.
Finally, Thailand had data in 30-minute intervals, which allowed us to model and pay particular attention to ramp rates.

## Slide 18
18
4.3.5 Status of flexibility enablers
4.3 Example case study
Source: IRENA (2019)
Notes: Next, we will assess the flexibility enablers within Thailand’s power system.
Here, “high” flexibility enabler values indicate very good conditions, ”medium" levels indicate normal conditions, and “low” levels indicate significant challenges or poor conditions for increasing power system flexibility at present. Some of these are labelled as N/A due to the system being modelled as a single node.
The interconnection capacity versus average demand is low. This is because, as previously mentioned, the interconnection capacity between external countries and Thailand is relatively small. However, Thailand possesses high generator ramping capabilities. This is due to the high amount of natural gas and hydro options.
Due to the low amount of variable renewable energy, matching demand with V.R.E. generation is medium. The storage versus annual demand is medium. The “high” rating of minimum demand versus V.R.E. capacity is due to the low amount of V.R.E. supply.
Finally, as previously mentioned, as this case study Thailand is modelled as a single node model, it is not possible to analyse the strength of the internal grid and geographical dispersion of V.R.E. generation and demand.

## Slide 19
19
Lecture 4.3 References
Ministry of Energy (2015), Alternative energy development plan, Thailand Ministry of Energy, Bangkok, http://www.eppo.go.th/images/POLICY/ENG/AEDP2015ENG.pdf
EGAT (2015), Thailand power development plan 2015-2036, Electricity Generating Authority of Thailand, Bangkok, https://www.egat.co.th/en/images/about-egat/PDP2015_Eng.pdf
IRENA (2017a), Renewable energy outlook: Thailand, International Renewable Energy Agency, Abu Dhabi.
IRENA (2019), Thailand power system flexibility assessment: IRENA FlexTool Case Study, International Renewable Energy Agency, Abu Dhabi.

## Slide 20
20
4.4.1 Dispatch in 2036
4.4 Analysing scenarios
Power generation (annual share) and hourly dispatch over a week in 2036, with the highest VRE penetration: Reference and REmap scenarios
Source: IRENA (2019)
Reference scenario reflects the official national plan, based on Thailand's existing Power Development Plan and stated policies.
REmap scenario represents a more ambitious vision, aligned with IRENA's REmap framework to significantly scale up renewables
Notes: On this slide, we see four figures. The top two figures refer to the 2036 reference scenario, whereas the bottom two figures refer to the REmap scenario.
The reference scenario shows that we have a majority of coal and gas, making up over 29% and 28% respectively. These are followed by over 18% of electricity provided by biogas and over 17% from hydro. There is a much smaller amount of solar and wind power generation, which both makeup over 2%. Finally waste provides over 1% of electricity.
When compared with the REmap scenario, we see an increase in solar photovoltaics and wind, at the expense primarily of coal and gas. Solar photovoltaics jumps from under 3% to just over 8%. Additionally wind makes up about 4% of dispatch.
The impact of flexibility on this can be seen by the graphs on the right. Whilst in the reference scenario photovoltaics reduces the amount of gas required on certain days, in the REmap scenario, solar reduces the use of gas on all days – sometimes down to zero.
Additionally, the REmap scenario displays a much more significant increase in the use of pumped hydro due to the storing of energy during the day and use during the night.

## Slide 21
21
4.4.2 Flexibility in 2036
4.4 Analysing scenarios
Main flexibility indicators for Thailand’s power system in 2036 reference and REmap scenarios
Source: IRENA (2019)
Notes: In this slide, we will explore the metrics used to measure whether there is enough flexibility in the system in both the reference and REmap scenarios.
These metrics are curtailment, loss of load, spillage, and reserves inadequacy.
Curtailment is where variable renewable energy sources are restricted in their output to prevent oversupply. Loss of load is when system load exceeds available generation; in other words, demand is larger than supply. Spillage occurs when the water inflow exceeds the amount that can be used by hydropower generators when reservoirs are full. Reserves inadequacy is when the reserve requirement cannot be met.
In all of these metrics, the results are zero. That means that with the combination of 12% of wind and solar, as shown in the previous slide, no flexibility issues were encountered.

## Slide 22
22
4.4.3 Evaluating additional investments
4.4 Analysing scenarios
Additional investments in wind and solar could save more than 2,000 million USD per year for Thailand, including investment costs
Source: IRENA (2019)
Notes: In this slide, we present the investment scenario.
Since no flexibility issues were identified in the 2036 reference and REmap scenarios, a sensitivity analysis was performed to check if there were cost-efficient additional investments. To do this, the expansion mode of FlexTool was used and identified that the minimum total system cost is achieved in the REmap scenario by adding 15GW of wind, 23.8 GW of solar, and 2 GW of biomass. This increases the variable renewable energy share from 12.3% to 33.4% (for example, photovoltaics and wind) and the renewable energy share, which also includes hydro and bio, from 49% to 74%. This can be seen in the Figure on the left-hand side which shows generation capacity.
The Figure on the right-hand side shows the total system costs with and without additional investments. The increased investment costs in wind, solar, and, to a lesser extent, biomass – as well as curtailment costs of 2%, are covered by savings in operational costs from fossil-fuelled capacity.

## Slide 23
23
4.4.5 Sensitivity analysis
4.4 Analysing scenarios
A sensitivity analysis was performed to investigate the impact of solar PV and wind on system flexibility.
In the reference and REmap scenario there are no curtailment and no flexibility issues.
In the REmap scenario with 40 GW of PV, VRE curtailment starts to appear (less than 0.5%).
Optimized investment REmap scenario yields 1.9% VRE curtailment.
Good match with hydro storage installed in the system.
VRE curtailment at different levels of solar and wind penetration in 2036
Source: IRENA (2019)
Notes: A sensitivity analysis was designed to investigate the impact of solar PV and wind on system flexibility. A sensitivity analysis is the systematic variation of key input parameters (e.g., demand, fuel cost, renewable availability, storage size) to observe how they affect the model’s solution and system performance.
For this sensitivity analysis, solar photovoltaics and wind are gradually added to test the system’s flexibility limits. In total, 34 variable renewable energy scenarios were simulated. The figure on the right shows variable renewable energy curtailment given different V.R.E. shares for 26 of the simulated scenarios.
As can be seen, with the reference and REmap scenario, there is no V.R.E. generation curtailment. Curtailment begins to appear in the REmap scenario with 40 gigawatts of photovoltaics and zero gigawatts of wind. However, the total curtailment is less than 0.5% which is at a reasonable level.
The optimized investment REmap scenario yields 1.9% level of curtailment.
The curtailment in the system begins to increase significantly after the 40 gigawatts of photovoltaic scenario or the 30 gigawatts of wind scenario. For example, the scenario modelling 40 gigawatts of photovoltaics and 30 gigawatts of wind reaches over 3% of curtailment.

## Slide 24
24
Lecture 4.4 References
IRENA (2019), Thailand power system flexibility assessment: IRENA FlexTool Case Study, International Renewable Energy Agency, Abu Dhabi.
IRENA (2020), IRENA FlexTool Basic Training, International Renewable Energy Agency, Abu Dhabi.

## Slide 25: Thank you
www.climatecompatiblegrowth.com