## Slide 1
Assessing power system flexibility with IRENA FlexTool
LECTURE 5
MODELLING FLEXIBILITY OPTIONS I

## Slide 2
2
Learning Outcomes
By the end of this lecture, you will be able to:
ILO1: Understand how to model flexible thermal generators.
ILO2: Understand how to model hydropower generators.
ILO3: Understand how to model energy storage systems.
ILO4: Understand how to model transmission.

## Slide 3
3
5.1.1 Examples of flexible thermal generators
5.1 Modelling flexible thermal generators
Flexible thermal generators are thermal power plants designed or operated to adjust their output quickly and reliably in response to changes in electricity demand or variable renewable energy (VRE) supply.
Open-cycle gas turbines (OCGTs)
Combined-cycle gas turbines (CCGTs)
Reciprocating internal combustion engines (RICEs)
Flexible coal-fired plants
Biomass and biogas-fired plants
Cogeneration (CHP) plants
Notes: Flexible thermal generators are thermal power plants designed or operated to adjust their output quickly and reliably in response to changes in electricity demand or variable renewable energy (VRE) supply. Technologies that are commonly considered flexible thermal generation include:
Open-cycle gas turbines (OCGTs) – Fast-start units capable of reaching full output within minutes, ideal for peak load and balancing VRE variability.
Combined-cycle gas turbines (CCGTs) with enhanced flexibility – Modern designs can reduce start-up times, operate efficiently at partial loads, and ramp up or down quickly.
Reciprocating internal combustion engines (RICEs) – Modular, fast-start generators that can follow rapid load changes and operate efficiently over a wide range of loads.
Flexible coal-fired plants – Upgraded coal plants with retrofits (e.g., improved control systems, advanced milling, sliding pressure operation) to allow lower minimum loads and faster ramping.
Biomass and biogas-fired plants – When equipped with responsive boiler and turbine controls, these can provide ramping and start-stop flexibility similar to fossil-fuel plants.
Waste-to-energy plants – If designed with flexible steam cycles, can modulate output to support grid balancing.
Cogeneration (CHP) plants – Especially gas-fired CHP systems that can vary electricity and heat output ratios in response to grid needs.
In many flexibility studies, gas turbines and reciprocating engines are considered the benchmark for fast, flexible thermal generation, while retrofit coal or biomass plants offer slower but still valuable flexibility for integrating higher shares of renewables.

## Slide 4
4
5.1.2 Parameterization
5.1 Modelling flexible thermal generators
a
c1
Technical characteristics of generation units are defined in the “unit_type” sheet.
Specific country/node capacity and fuels of those unit types are defined in “units” sheet.
To add a technology:
    Add a new row in the “unit_type” and specify all the necessary technical characteristics
    Add a new row in “units” and then choose the technology from unit type list.
    Specify the input to the generator which can be fuel, cf-factor (for solar or wind), inflow (hydro), or an energy vector, such as electricity or heat from an input grid
    Specify the output grid and location
    Specify the Installed capacity and Max investment (invest mode only)
b
c2
c3
c4
c5
Notes: Technical characteristics of generation units are defined in the “unit_type” sheet, as shown in the first figure. Here you can add new technologies or modify the flexibility characteristics of different technologies such as ramping capability, inertia constant, minimum stable load, etc. Then in the “units” sheet, you can set the capacity of those units and the node they are located as shown in the bottom figure. Here the structure of the grids and the flow of fuels or energy vectors are set.
For example, to specify the generation capacity in node A, you should first add an empty row, then select the technology under the column unit type. Please note that dark blue cells have dropdown menus to choose names defined in violet or green cells in other sheets. For each technology, you should then choose the type of fuel from the list. If the technology is variable solar or wind, you should add the capacity factor. This is the available output at each time step for each unit of capacity installed. Next, add the capacity factor in the column cf profile. The capacity factor profiles for solar and wind can be found and updated in the ”ts-cf” sheet. For some technologies, such as hydro, the inflow should be specified. Then the output grid should be set. In the case of power generators, the output grid is the electricity grid. After that, the location of plants or the output node should be set. The capacity is the total capacity of that technology installed in the output node. Therefore if only a single node is used to represent a country, this will be the total installed capacity of that technology in the country. If a country is divided into different nodes, then the capacity of each technology at each node should be specified separately. You can also set the maximum investment for each technology, which is the maximum capacity that the model can invest in the specified output node. For example, in this case, the maximum installed capacity of PV in node A cannot be more than 500 MW. Evidently, the total maximum capacity of PV for the whole country is the sum of maximum PV capacities in all nodes.

## Slide 5
5
Lecture 5.1 References
IRENA. 2019. IRENA FlexTool Modelling different flexibility options. International Renewable Energy Agency, Abu Dhabi. https://www.irena.org/-/media/Irena/Files/IRENA-flextool/IRENA_FlexTool_FlexibilityOptions.pdf

## Slide 6
6
5.2.1 Hydropower generators
5.2 Modelling hydropower generators
According to the International Hydropower Association, hydropower projects are generally classified into three main types: Run-of-river hydropower, reservoir hydropower, and pumped hydro storage.
Source: Euroelectric (2024)
Notes: According to the International Hydropower Association, hydropower projects are generally classified into three main types, although these technologies can overlap in practice. For example, a storage plant may incorporate pumping systems to supplement natural inflows to the reservoir, and a run-of-river facility may include limited storage capacity.
Run-of-river hydropower: This type channels flowing river water through a canal or penstock to drive a turbine. It typically has little or no storage, providing a continuous electricity supply (base load) with some operational flexibility to manage daily demand fluctuations by regulating water flow.
Storage hydropower: Usually implemented as a large-scale system with a dam that stores water in a reservoir. Power is generated by releasing water through turbines, activating a generator. These plants can provide both base load and peak load, as they can be started or stopped quickly according to system demand. They often have sufficient storage to operate independently of natural inflows for weeks or even months.
Pumped storage hydropower: Designed primarily for peak-load supply, this type cycles water between an upper and lower reservoir. During periods of low demand, surplus electricity is used to pump water to the upper reservoir. When demand is high, the stored water is released back through turbines to generate electricity.

## Slide 7
7
5.2.2 Parameterization I
5.2 Modelling hydropower generators
a
b
d
Source: IRENA 2020a
Two types of hydro generators can be modelled in FlexTool:
Run of the river hydro (Hydro_ROR): It is similar to defining a thermal generator with some differences:
The natural inflow times series (MWh/h) should be defined in the “ts_inflow” sheet
Assign the inflow to hydro-ROR unit in “units” sheet by selecting inflow input option.
Define inflow multiplier (1 as default) in “units” sheet.
Hydro with reservoir (Hydro_RES): In addition to steps for Hydro_ROR
d) a value for the storage capacity should be set in “storage (MWh)” column in the “units” sheet.
Notes: Hydropower is the most flexible generator in many regions. It has a swift response rate and very flexible operation; however, the capacity of hydro units can vary with the annual precipitation level. Two types of hydro generators can be modelled in FlexTool, Run of the river hydro, which usually does not have storage capability, and Hydro with reservoir. Defining hydropower is similar to other generators, but some additional steps are required. First, you should define the natural inflow data in the “ts_inflow” sheet. Then in the sheet “unit”, it should be assigned as the inflow to hydro units.
Hydro units are similar to solar and wind units but use “ts_inflow” data instead of “ts_cf” as input. Set the inflow multiplier to 1 in the sheet “units”. In addition to previous steps, for Hydro with reservoir, you should also specify the total storage capacity in MW in each output node. You can also define the storage level at the start and finish time steps. But this is optional, and if it is left empty, the start level should equal the finish level.
For pumped hydro storage, the technology can be represented in the model as a storage system analogous to a battery, with further details provided in the next section.

## Slide 8
8
5.2.3 Parameterization II
5.2 Modelling hydropower generators
To add hydro to an output node:
An inflow profile should be added to the “ts_inflow” sheet.
Set the name in this format: “output node_Hydro technology”, e.g. nodeB_RES
The data will then appear in the inflow dropdown menu list and can be assigned to the associate hydro technologies and output nodes.
Same steps should be followed to add variable renewables in different nodes.
c
a
Notes: In order to add Hydro in different nodes, first, the inflow profile should be defined in the “ts_inflow” sheet. You should then specify the name. It is recommended to set the names in this format: “output node_Hydro technology”, for example, node B_R E S. The data will then appear in the inflow dropdown menu list and can be assigned to the associate hydro technology and the output node. If the added Hydro has storage capability, the storage capacity should also be specified for the output node.
The same steps can be followed to add variable renewables to different nodes using the “ts_cf” sheet.

## Slide 9
9
9
Lecture 5.2 References
IRENA. 2019. IRENA FlexTool Modelling different flexibility options. International Renewable Energy Agency, Abu Dhabi. https://www.irena.org/-/media/Irena/Files/IRENA-flextool/IRENA_FlexTool_FlexibilityOptions.pdf
Euroelectric. 2024. The hidden power of water: flexibility. https://www.eurelectric.org/news/hydropower_flexibility/

## Slide 10
10
5.3.1 Energy storage systems
5.3 Modelling storage
Thermal energy storage
Ex: Sensible heat storage using molten salts
Mechanical energy storage
Ex: Pumped hydro energy storage
Chemical energy storage
Ex: Hydrogen energy storage
Electrochemical energy storage
Ex: Battery energy storage
Electrical-magnetical energy storage
Ex: Supercapacitors
Others
Ex: Hybrid energy storage
Notes: Energy storage systems (ESS) are essential to the energy transition as they address the intermittency of renewable energy sources like solar and wind, enabling their integration into the grid. By storing excess energy during periods of low demand and releasing it during peak times, ESS ensures a consistent and reliable energy supply. The figure presents a classification of ESS based on the primary physical or chemical principle they employ. Thermal energy storage involves capturing and retaining heat for later use, such as sensible heat storage with molten salts, which is common in concentrated solar power plants. This method allows the stored thermal energy to be converted back into electricity or used directly for heating. Mechanical energy storage includes systems like pumped hydro energy storage, where energy is stored by moving water between two reservoirs at different elevations, and later released to generate electricity during peak demand.
Chemical energy storage refers to storing energy in chemical bonds, such as hydrogen production through electrolysis. The stored hydrogen can later be used in fuel cells or combustion processes to generate electricity. Electrochemical energy storage encompasses technologies like batteries, where energy is stored in chemical form within cells and released through electrochemical reactions. Batteries are highly versatile, with applications ranging from grid balancing to electric vehicles.
Electrical–magnetic energy storage includes systems like supercapacitors, which store energy in an electric field rather than through chemical reactions, enabling very rapid charging and discharging. The others category covers hybrid energy storage systems, which combine two or more storage technologies to leverage complementary strengths—for example, pairing batteries with supercapacitors to combine high energy capacity with fast response times. Together, these categories capture the wide range of technological approaches available for storing energy to enhance power system flexibility and reliability.

## Slide 11
11
5.3.2 Parameterization I
5.3 Modelling storage
Power storage is defined in the “unit_type”, with some additions compared to other generators:
  Efficiency(%): Discharging efficiency
  Eff.charge(%): Charging efficiency
  Self-discharge loss (% of content per hour)
Same as other units in the “units” sheet the following parameters should be defined:
d) Installed capacity in MW
e) The output node
f) Maximum storage capacity in MWh
g) Initial and final state of the storage (optional)
a
b
c
d&e
f
g
Notes: Electricity storage units should also be defined as the same as other generators with some minor differences. For power storage units, you should define separate charging and discharging efficiencies. Also, for some types of storage, you may need to specify the self-discharge loss, which is the loss of stored energy from storage at each hour. Batteries have instantaneous response rate and can ramp up or ramp down their output quickly. Therefore you can set the ramp rates to 1.
The other important point about batteries is that they are non-synchronous units, the same as PV and wind. Therefore this column should be set to 1.
In the “units” sheet, you should define Installed capacity in MW, Output node, and Maximum storage capacity in MWh. You can also define the initial and final state of the storage but they are optional.
If storage type is pumped hydro storage it is possible that the unit has a natural inflow, which could be defined in “ts_inflow” sheet.

## Slide 12
12
5.3.3 Parameterization II
5.3 Modelling storage
There are two options for defining investment for electricity storage units:
Fix power to energy ratio:
It will use a fixed discharge duration for battery units. For example, in the example the model only considers 2-hour duration batteries in optimisation.
Only investment cost per energy (kWh) should be defined in this case.
b) Free optimisation of power and energy:
Optimises power and energy separately, and there is no need to define the power/energy ratio
Both investment cost for power and energy should be defined.
a
b
Notes: There are two options for defining investment for electricity storage units: the first way is to fix the power to energy ratio. This will fix the discharge duration for storage units, for example, 2-hour or 4-hour units. In other words, the model only considers storage units with this fixed discharge duration. The only investment cost required in this case is the investment per energy stored. The second option is to use a free optimization of power and energy. In this case, there is no need to define a power to energy ratio, and you should set the investment required per unit energy and investment per unit power. The model optimizes power and energy separately. That is to say; the model can use storage units with different storage durations.

## Slide 13
13
Lecture 5.3 References
IRENA. 2019. IRENA FlexTool Modelling different flexibility options. International Renewable Energy Agency, Abu Dhabi. https://www.irena.org/-/media/Irena/Files/IRENA-flextool/IRENA_FlexTool_FlexibilityOptions.pdf

## Slide 14
14
5.4.1 Transmission as flexibility option
5.4 Modelling transmission
Enables regional balancing by transferring electricity between areas, smoothing variability in renewable generation and demand.
Reduces curtailment, shortages, and operational stress by delivering surplus energy to high-demand regions, importing during local deficits, and sharing system inertia when AC interconnections are in place.
Enhances system efficiency through reserve sharing, congestion reduction, and optimal dispatch of least-cost generation.
Notes: Transmission plays a critical role in enhancing the flexibility of a power system because it enables the movement of electricity across regions, allowing generation and demand to be balanced over a wider geographic area. A stronger and more interconnected transmission network can help absorb variability from renewable energy sources by pooling diverse generation profiles, such as solar from one region and wind from another, so that fluctuations in one area can be offset by stable supply from another. This reduces the need for local balancing resources and helps maintain system reliability.
From a flexibility perspective, transmission expands the range of available resources for system operators. For example, when there is surplus renewable generation in one part of the grid, transmission lines allow that electricity to be delivered to regions experiencing higher demand, avoiding curtailment. Similarly, during periods of scarcity in one area, imports from other regions or countries can prevent load shedding and reduce reliance on expensive peaking plants. This spatial balancing capability is especially valuable in integrating high shares of variable renewable energy (VRE).

## Slide 15
15
5.4.1 Modelling nodes
5.4 Modelling transmission
It is possible to model different networks in the “gridNode” : e.g., Electricity network, gas network, heat network, etc.
For all the nodes on each grid you should specify:
The demand
Import and export
The capacity margin
The nodes can be grouped together in order to set whole system
constraints in “Nodegroup”
For each group you should specify:
d. Capacity margin
e. Maximum non-synchronous share
f. Inertia requirements
g. Availability of reserve
h. You can assign the node groups to different nodes in the “gridNode”
b
a
c
d
e
f
g
h
Notes: You can model different networks such as gas grid, electricity grid and heat network, in the “gridNode” sheet. Each grid can be represented by a single node or multiple nodes representing different regions on a grid. The grid can also cover only some regions. For all the nodes of a grid, you should specify the aggregated demand in each node, whether there is import or export, and their capacity margin. Nodes can be grouped in order to set whole system constraints such as inertial requirements, total system capacity margin requirements, etc. You can define the node groups in the “Nodegroup” sheet. Then you can specify the group specifications such as the inertial requirement, maximum non-synchronous share, capacity margin requirements, and availability of reserve. You can assign the groups to different grids in the “gridNode” sheet.

## Slide 16
16
5.4.2 Parameterization
5.4 Modelling transmission
Node A
Node B
Transmission links between nodes of each network are defined in the “nodeNode” sheet.
Both nodes on a connecting link have to be from the same grid
Existing transmission links can have different capacities in different directions.
Future investments will always have equal capacity in both directions.
Notes: The transmission links between nodes of each network are defined in the “nodeNode” sheet. All the available links between different nodes should be defined here. When defining the linking between nodes, it is important to note that both nodes have to be from the same grid. The existing transmission links can have different capacities in different directions; however, further investments will always have equal capacities in both directions.

## Slide 17
17
5.4.1 Modelling transmission losses
5.4 Modelling transmission
Node B
Node A
v transfer
v transfer rightward
v transfer leftward
Transmission with losses requires at least two variables
  A linear equation with ‘loss x transfer’ would mean that in the other direction loss is actually a gain
The loss can be used to make the model leak
  Instead of curtailing VRE, the model can dissipate energy by transferring in two directions at once
  Can be controlled only with a binary variable (not allowed in FlexTool)
Hence, three variables (v): transfer, transfer rightward, and transfer leftward
  Transfer does not contain loss
  Transfer rightward allows losses and helps to limit the leakage
  Transfer leftward helps to limit the leakage further
Notes: Modelling transmission with losses requires at least two variables. If only one linear equation is used, such as ‘loss x transfer’, it would mean that in the other direction loss is actually again. The loss variable can be used to make the model ‘leak’. Therefore instead of curtailing variable renewable energy, the model can dissipate energy by transferring in two directions at once. The loss can be controlled only with a binary variable, but that is not allowed in FlexTool. Hence three variables are defined: transfer, transfer rightward, and transfer leftward
The first one is the transfer does not contain loss
The second is the transfer rightward allows losses and helps to limit the leakage
The third is the transfer leftward helps to limit the leakage further

## Slide 18
18
Lecture 5.4 References
IRENA. 2019. IRENA FlexTool Modelling different flexibility options. International Renewable Energy Agency, Abu Dhabi. https://www.irena.org/-/media/Irena/Files/IRENA-flextool/IRENA_FlexTool_FlexibilityOptions.pdf

## Slide 19: Thank you
www.climatecompatiblegrowth.com